8

7

9

4

5

6

1

2

3

-

0

.









A















MCU CLIMAT

(V5.03)

Programming Guide

This document may not be copied, reproduced or distributed in any form or by any means whatsoever without our prior consent. Although care has been taken to ensure accuracy we cannot assume responsibility for the consequences of any errors or omissions that may be contained herein. All illustrations are provided for information only and are non contractual.

This document does not contain any warranty statement. Please refer to our General Terms and Conditions of Sale.

CONTENTS

1	INTRODUCTION	1-1

1.1	Control Panel	1-1

1.2	Power Up Display (Global)	1-1

1.3	Installed Program Details (Global)	1-2

1.4	Menu tree outline	1-3

2	DAY-TO-DAY MONITORING	2-1

2.1.1	T°, RH and Vents	2-1

2.1.2	Heating	2-2

2.1.3	Averages	2-3

2.1.4	Influences On Vents	2-3

2.1.5	Influences On Heating	2-4

2.1.6	Boiler Status	2-5

3	ALARMS	3-1

3.1	Readings	3-1

3.2	Activation Thresholds	3-2

Enable compartment alarms	[ Yes / No ]	3-2

Minimum compart temperature	[ -10/+40 °C ]	3-2

Maximum compart temperature 	[ -10/+40 °C ]	3-2

Max T increase at max radiation	[ -10/+40 °C ]	3-2

Minimum compartment humidity 	[ 0 – 100 % ]	3-2

Maximum compartment humidity 	[ 0 – 100 % ]	3-2

Minimum ground temperature	[ -10/+40 °C ]	3-2

Maximum ground temperature	[ -10/+40 °C ]	3-2

Min CO2 level activate alarm	[ 0 – 20000 ppm ]	3-2

Max CO2 level activate alarm	[ 0 – 20000 ppm ]	3-2

Alarm time delay	[ 0 – 1440 min ]	3-2

4	ACCESS CODES	4-1

4.1	Levels	4-1

4.2	Setting up control	4-1

5	PERIODS	5-1

5.1	Setting up control	5-1

5.1.1	Start time attachment	5-1

5.2	Transition Times	5-1

6	WEATHER MONITORING STATION	6-1

6.1	Settings	6-1

Rain detection threshold	[ 0 – 100 % ]	6-1

Delay before deactivate rain	[ 0 – 240 min ]	6-1

Frost detection threshold	[ -25/+40 °C ]	6-1

Storm wind speed threshold	[ 0 – 72 km/h ]	6-1

Delay before deactivate storm	[ 0 – 240 min ]	6-1

Sync. vents if storm detected	[ Yes / No ]	6-1

Fix vent pos storm detected	[ Yes / No ]	6-1

N° of o/p activate storm conditions	[ 0 – 256  ]	6-1

Threshold for maximum wind speed	[ 0  – 150 Km/h ]	6-1

Wind speed tolerance	[ 0  – 150 Km/h ]	6-1

Time maintain max wind speed	[ 0 – 500 min ]	6-1

Calc. wind speed average over	[ 0 – 20 min ]	6-1

Calc. sol. radiation average over	[ -10 /+10 min ]	6-1

6.1.1	Configuring the wind speed reading	6-1

6.1.2	Configuring the solar radiation reading	6-1

6.2	Wind Influences	6-2

Wind dir. change timeout	[ 0 – 500 min ]	6-2

Wind speed for min influence	[ 0 – 72 km/h ]	6-2

Wind speed for max influence	[ 0 – 72 km/h ]	6-2

Max infl. on w. dir. timeout	[ 0 – 500 min ]	6-2

6.3	Rain gauge (option only)	6-2

Volume of water per pulse	[ 0 – 10000 mm ]	6-2

Sensor surface area	[ 0 – 10000 cm² ]	6-2

7	VENTS	7-1

7.1	Setting up control	7-1

Ventilation temperature	[ -10/+ 40 °C ]	7-1

Ventilation temperature offset	[ 0 – 40 °C ]	7-1

Maximum vent position	[ 0 – 100 % ]	7-1

Minimum vent position	[ 0 – 100 % ]	7-1

7.2	Influences	7-1

7.2.1	Outside temperature	7-1

Outside T for start of influ.	[ -25/+40 °C]	7-1

Outside T for max influence	[ -25/+40 °C]	7-1

Max influ. on p-band temp	[ 0 – 5 °C ]	7-1

Max influ. on max vent pos	[ 0 – 100% ]	7-1

Min percentage corr. max pos	[ 0 – 100% ]	7-1

Influ. on min vent position	[ Yes / No ]	7-1

7.2.2	Wind speed	7-2

Min wind speed influence	[ 0 – 72 km/h ]	7-2

Max wind speed influence	[ 0 – 72 km/h ]	7-2

Max influ. on p-band temp	[ 0 – 50 °C ]	7-2

Max influ. on max vent pos	[ 0 – 100% ]	7-2

Min percentage corr. max pos	[ 0 –  100% ]	7-2

Influ. on min open position	[ Yes / No ]	7-2

7.2.3	Solar radiation	7-2

Rad. for minimum influence	[ 0 – 1000 W/m² ]	7-2

Rad. for maximum influence	[ 0 – 1000 W/m² ]	7-2

Max infl. on ventilation temp	[ -40 /+40 °C ]	7-2

Max influ. on max vent position	[ -100 /+100 % ]	7-2

Min percentage correction pos max	[ 0 – 100 % ]	7-2

Overshoot max open pos	[ Yes / No ]	7-2

Start time	[ 00:00 - 23:59 ]	7-2

End time	[ 00:00 - 23:59 ]	7-2

7.3	Safety Settings	7-3

Max position rain detected	[ 0 – 100 % ]	7-3

Max position frost detected	[ 0 – 100 % ]	7-3

Max position storm detected	[ 0 – 100 % ]	7-3

Vent alarm delay	[ 0 – 120 min ]	7-3

Percentage error for alarm	[ 0 – 100 % ]	7-3

O/s humidity close vents, drying	[ 0 – 100 % ]	7-3

7.4	General Configuration	7-3

Control temp difference	[ 0 – 40°C ]	7-3

Vent control interval	[ 0 – 120min ]	7-3

Min percentage correction	[ 0 – 50% ]	7-3

Min percentage corr. at 100%	[ 0 – 50% ]	7-3

Max percentage correction	[ 0 – 100% ]	7-3

Vent p-band T at 100% (lee)	[ 0 – 50°C ]	7-3

Vent p-band T at 100% (wind)	[ 0 – 50°C ]	7-3

Cumulative percent. correction	[ 0 – 100% ]	7-3

Trend percentage correction	[ 0 – 100% ]	7-3

P-band based on max pos	[ Yes / No ]	7-3

7.5	Physical Configuration	7-4

Overall time to open	[ 0 – 1200 sec ]	7-4

Overall time to close	[ 0 – 1200 sec ]	7-4

Number of vent to follow	[ 0 – N vents ]	7-4

Time after end travel 	[ 0 – 300 sec ]	7-4

Temperature sensor	[ T1 / T2 / T1,T2]	7-4

Vent position sensor 	[ Yes / No ]	7-4

Sensor error correction	[ 50 - 1000 ]	7-4

7.6	Compartment Orientation	7-4

Compartment orientation	[ 0 – 360° C]	7-4

7.7	Synchronization	7-4

Synchronization time	[ 00:00 – 23:59 ]	7-4

Synchronization time	[ 00:00 – 23:59 ]	7-4

Max position start synchronization	[ 0 – 100% ]	7-4

Synchronization interval	[ 0 – 1440 min ]	7-4

Synchronization at 0 %	[ Yes /No ]	7-4

8	HumidIty control	8-1

8.1	Introduction	8-1

8.2	Set-point Monitoring	8-2

8.3	Setting Up Control	8-2

Lower sat. deficit limit	[ 0 - 50  mBar ]	8-2

Upper sat. deficit limit	[ 0 - 50  mBar ]	8-2

Maximum permitted temperature	[ 0 - 50  °C ]	8-2

Minimum permitted temperature	[ 0 - 50  °C ]	8-2

Vent control delay	[ 0 – 1440 min ]	8-2

Drying cycle interval	[ 0 – 1440 min ]	8-2

Max T° diff. min RH infl. on vents	[ 0 – 40 °C ]	8-2

Stop heating for T°/RH max	[ Yes / No ]	8-2

Humidity control mode	[ 1, 2, or 3 ]	8-2

Min humidity influence on Max Pos	[ Yes / No ]	8-2

Lee / Wind sequence	[ Yes / No ]	8-2

8.4	Influences On Vent Control	8-3

Hum influence on vent position	[ 0 – 10 %/% ]	8-3

Max vent pos for RH influ	[ 0 – 100 % ]	8-3

Reduction max pos, o/s T° influ.	[ 0 – 100 % ]	8-3

Reduction max pos, wind influ.	[ 0 – 100 % ]	8-3

Min humid. influ. on vent position	[ 0 – 10 %/% ]	8-3

Diff max vent pos min humid. Influ.	[ 0 – 100 % ]	8-3

Maximum humidity 	[ 0  - 100% ]	8-3

Minimum humidity 	[ 0  - 100% ]	8-3

Minimum deficit 	[ 0 - 50  mBar ]	8-3

Maximum deficit 	[ 0 - 50  mBar ]	8-3

8.5	Influences On Heating	8-3

Influ. on water temperature	[ 0 – 130 °C/% ]	8-3

Max infl on calculated water T	[ 0 – 130 °C ]	8-3

Influence Hmin. on water temp.	[ +/- 130 °C/% ]	8-3

Max influ on calculated water T	[ 0 – 130 °C ]	8-3

Influence Hmin. on min water temp.	[+/- 130 °C/%]	8-3

Max influ on minimum water T	[ 0 – 130 °C ]	8-3

9	HOT WATER HEATING	9-1

9.1	Setting Up Control	9-1

Ambient temperature 	[ -10/+40 °C ]	9-1

Ground temperature	[ -10/+40 °C ]	9-1

Minimum water temperature	[ 0 – 90 °C ]	9-1

Maximum water temperature	[ 0 – 130 °C ]	9-1

9.2	Influences	9-2

9.2.1	Outside temperature	9-2

Outside T° for min influence	[ -25/+20 °C ]	9-2

Outside T°  for max influence	[ -25/+20 °C ]	9-2

Max infl. on min water temp	[ 0 – 50  °C ]	9-2

9.2.2	Wind speed	9-2

Wind speed for min influence	[ 0 – 72 km/h ]	9-2

Wind speed for max influence	[ 0 – 72 km/h ]	9-2

Max infl. on min water temp	[ 0 – 50 °C ]	9-2

9.2.3	Solar radiation	9-2

Time start influence active	[ 00:00 - 23:59 ]	9-2

Time end influence active	[ 00:00 - 23:59 ]	9-2

Radiation for min influence	[ 0 – 1000 W/m² ]	9-2

Radiation for max influence	[ 0 – 1000 W/m² ]	9-2

Max influence on ambient temp.	[ -40/+40  °C ]	9-2

Max influence on min water temp.	[ -100/+100  °C ]	9-2

Accum. radiation for min influence	[0 – 1000 Wh/m² ]	9-2

Accum. radiation for max influence	[0 – 1000 Wh/m² ]	9-2

Max influence on ambient temp.	[ -40/+40  °C ]	9-2

Max influence on ventilation temp.	[ -40/+40  °C ]	9-2

Time start influence active	[ 00:00 - 23:59 ]	9-2

Time end influence active	[ 00:00 - 23:59 ]	9-2

9.3	Configuration	9-3

Heating control interval	[ 0 – 30 min ]	9-3

Ki, control point coefficient	[ 0 - 10 ]	9-3

Kd, heating trend coefficient 	[ 0 - 100 ]	9-3

Kp, water temp coefficient	[ 0 - 10 ]	9-3

Max water T var. per interval	[ 0 - 10 °C]	9-3

Water T diff. to control 3WV	[ 0 - 10 °C ]	9-3

Min 3WV control time per °C	[ 0 – 120 sec ]	9-3

Max 3WV control time per °C	[ 0 – 120 sec ]	9-3

Water T° diff. infl min ctrl time	[ 0 – 130 °C ]	9-3

Water T° diff. infl max ctrl time	[ 0 – 130 °C ]	9-3

3WV overall control time	[ 0 – 120 sec ]	9-3

Open 3WV (at boiler 3WV temp)	[ Yes / No ]	9-3

Heating pump ON, water temp	[ 0 – 130 °C ]	9-3

Heating pump ON, ambient temp	[ 0 – 130 °C ]	9-3

3WV and pump service interval	[ 0 – 500 hr ]	9-3

Flow rate for energy calc.	[ 0 - 1000 m3/h]	9-3

Stop pump at blr T closes 3WV	[ Yes / No ]	9-3

Delay before pump stops	[ 0 – 1440 min ]	9-3

Temperature sensor	[T1,T2,T1/T2, Ts ]	9-3

Number of compartment to follow	[ ]	9-3

9.4	Safety settings	9-4

Amb. T° diff. cancels min wtr T	[ 0 – 50 °C ]	9-4

Water T diff. triggers alarm	[ 0 – 130 °C ]	9-4

Alarm delay	[ 0 – 1440 min ]	9-4

10	BOILER CONTROL	10-1

10.1	Setting Up Control	10-1

Boiler on line 	[ Yes / No ]	10-1

Min water temp limit for alarm 	[ 0 – 130 °C ]	10-1

Max water temp limit for alarm	[ 0 – 130 °C ]	10-1

Delay before alarm activates	[ 0 – 1440 min ]	10-1

Water temp closes valves	[ 0 – 130 °C ]	10-1

Water temp opens valves	[ 0 – 130 °C ]	10-1

Minimum water temperature	[ 0 – 130 °C ]	10-1

Maximum water temperature	[ 0 – 130 °C ]	10-1

Water T diff. stops burner	[ 1 – 130 °C ]	10-1

Boiler water temp increase	[ 0 – 100 % ]	10-1

Min return water temp. alarm	[ 0 – 130 °C ]	10-1

Max return water temp. alarm	[ 0 – 130 °C ]	10-1

10.2	Configuration	10-2

Burner control interval	[ 0 –  60 sec  * 5 ]	10-2

Kp boiler coeff. (sec/ 1deg)	[1 – 10 sec/1deg ]	10-2

Kd boiler coeff. (sec/ 1deg)	[1 – 10 sec/1deg ]	10-2

Difference starts burner	[ -50/+50 °C ]	10-2

Initial burner control delay	[ 0 – 600 sec ]	10-2

Overall burner control time	[ 0 – 1200 sec ]	10-2

Minimum boiler ON time	[ 0 – 600 sec ]	10-2

Max burner pos, aux period	[ 0 – 100 % ]	10-2

Burner position deviation	[  ]	10-2

Burner alarm delay	[  ]	10-2

Burner position input n°	[  ]	10-2

Recirculating pump output n°	[  ]	10-2

Recirculating pump ON time	[  ]	10-2

ON/OFF output n° (stop modul)	[  ]	10-2

10.3	Twin Firing Boiler	10-3

T diff. for high firing	[ 0 – 50 °C ]	10-3

Delay before starting	[ 0 – 3600 sec ]	10-3

Max permitted outside temp	[ -25/+40 °C ]	10-3

T° diff stops high firing	[ 0 – 130 °C ]	10-3

Time before return to normal firing	[ 0 – 3600 sec ]	10-3

Kp boiler (sec/ 1deg)	[1 – 10 sec/1deg ]	10-3

Kd boiler (sec/ 1deg)	[1 – 10 sec/1deg ]	10-3

Initial burner control delay	[ 0 – 600 sec ]	10-3

Overall burner control time	[ 0 – 1200 sec ]	10-3

10.4	Special Operating Modes	10-3

Start of auxiliary period	[ 00:00 – 23:59 ]	10-3

End of auxiliary period	[ 00:00 – 23:59 ]	10-3

Auxiliary period boiler temp	[ 0 – 130 °C ]	10-3

Close boiler valve during aux per	[ Yes / No ]	10-3

Close valve boiler deactivated	[ Yes / No ]	10-3

11	HEATING TRANSPORT LINES	11-1

11.1	Setting up control	11-1

Minimum water temperature	[ 0 – 130 °C ]	11-1

Maximum water temperature	[ 0 – 130 °C ]	11-1

Transport  water temp increase	[ 0 – 50 °C ]	11-1

Water temperature alarm delay	[ 0 – 120 min ]	11-1

11.2	Influences	11-1

11.2.1	Outside temperature	11-1

Outside T° for start of influence	[ -25/+40 °C ]	11-1

Outside T for max influence	[ -25/+40 °C ]	11-1

Max infl. on min water temp	[ 0 – 130 °C ]	11-1

Outside T° for start of influence	[ -25/+40 °C ]	11-1

Outside T for max influence	[ -25/+40 °C ]	11-1

Max infl. on min water temp	[ -130/+130 °C ]	11-1

Temperature sensor input number	[ 0 – 256 ]	11-1

Water T° increase, forced CO2	[ 0 – 100 % ]	11-1

Time start frost heating	[ 00:00 – 23:59 ]	11-1

Time end frost heating	[ 00:00 – 23:59 ]	11-1

O/s T° activate function	[ -25/+40 °C ]	11-1

Heating temperature	[ 0 – 130 °C ]	11-1

Heating ON, rain detected	[ Yes / No ]	11-1

11.2.2	Forced CO2 heat storage	11-1

11.2.3	Frost and snow influence	11-1

11.3	Hot Water Storage	11-2

Storage starts	[ 00:00 – 23:59 ]	11-2

Storage ends	[ 00:00 – 23:59 ]	11-2

Number degrees of storage	[ -130/+130 °C ]	11-2

Storage interval	[ 0 – 1200 min ]	11-2

Storage starts	[ 00:00 – 23:59 ]	11-2

Storage ends	[ 00:00 – 23:59 ]	11-2

Number degrees of storage	[ -130/+130 °C ]	11-2

Storage interval	[ 0 – 1200 min ]	11-2

11.4	Configuration	11-2

Temp diff. to control 3WV pos	[ 0 –10 °C ]	11-2

3WV control time per degree C	[ 0 – 120 sec ]	11-2

3WV overall control time	[ 0 – 1200 sec ]	11-2

Heating pump on, water temp	[ 0 –130 °C ]	11-2

Stop pump (Economy)	[ Yes / No ]	11-2

Pump and 3WV service interval	[ 0 – 500 h ]	11-2

3WV control interval	[ 1 – 60 min ]	11-2

Diff (Tamb,Tventil) stops pump	[ -50/+50 °C ]	11-2

Open 3WV at blr T° opens 3WV	[ Yes / No ]	11-2

Min. position 3WV	[ 0 – 100 % ]	11-2

Input number for position 3WV 	[ 1 – 256 ]	11-2

Transport T° activate 2nd pump	[ -130/+130 °C ]	11-2

Delay before pump stops	[ 0 – 900 min ]	11-2

Return T° activates 2nd  pump	[ Yes / No ]	11-2

Temp diff. starts 2nd pump	[ -130/+130 °C ]	11-2

Minimum ON time	[ ]	11-2

Switch pump 1 /2 	[ Yes / No ]	11-2

Pump interval 1 /2 	[ 0 – 30000 sec ]	11-2

11.4.1	Temperature Sensor Configuration	11-3

Measurement percentage, sensor n°1	[ 0 – 100 % ]	11-3

Measurement percentage, sensor n°2	[ 0 – 100 % ]	11-3

Measurement percentage, sensor n°3	[ 0 – 100 % ]	11-3

12	CO2 DOSING	12-1

12.1	Setting up control	12-1

Enable CO2 injections	[ Yes / No ]	12-1

Start time	[ 00:00 – 23:59 ]	12-1

Start time	[ 00:00 – 23:59 ]	12-1

Start time	[ 00:00 – 23:59 ]	12-1

Start time	[ 00:00 – 23:59 ]	12-1

End time	[ 00:00 – 23:59 ]	12-1

Min CO2 level activate alarm	[ 0 – 20000 ppm ]	12-1

Max CO2 level activate alarm	[ 0 – 20000 ppm ]	12-1

Free CO2 threshold	[ 0 – 20000 ppm ]	12-1

Free CO2 threshold	[ 0 – 20000 ppm ]	12-1

Free CO2 threshold	[ 0 – 20000 ppm ]	12-1

Free CO2 threshold	[ 0 – 20000 ppm ]	12-1

Forced CO2 threshold	[ 0 – 20000 ppm ]	12-1

Forced CO2 threshold	[ 0 – 20000 ppm ]	12-1

Forced CO2 threshold	[ 0 – 20000 ppm ]	12-1

Forced CO2 threshold	[ 0 – 20000 ppm ]	12-1

Liquefied CO2 threshold	[ 0 – 20000 ppm ]	12-1

Liquefied  CO2 threshold	[ 0 – 20000 ppm ]	12-1

Liquefied  CO2 threshold	[ 0 – 20000 ppm ]	12-1

Liquefied  CO2 threshold	[ 0 – 20000 ppm ]	12-1

Min deficit for injection	[ 0 – 50 mBar ]	12-1

Max deficit for injection	[ 0 – 50 mBar]	12-1

Max  injection time	[ 0 – 1400 min ]	12-1

CO2 measurement sample time	[ 0 – 1200 sec ]	12-1

Heating water temp increase	[ 0 – 100 % ]	12-1

Stop free CO2, use for forcing 	[ Yes / No ]	12-1

Maximum permitted temperature	[ -10/+40 °C ]	12-1

Min OFF time, liquid CO2 inj.	[ 0 – 1400 min ]	12-1

Max injection time, liquid CO2	[ 0 – 1400 min ]	12-1

Minimum ON time	[ 0 – 1400 min ]	12-1

Minimum OFF (pause) time	[ 0 – 1400 min ]	12-1

12.2	Various Influences	12-2

12.2.1	Solar radiation	12-2

Rad. for minimum influence	[ 0 – 1000 W/m² ]	12-2

Rad. for maximum influence	[ 0 – 1000 W/m² ]	12-2

Max infl. on free CO2 threshold	[ 0 – 20000 ppm ]	12-2

Max infl. on forced CO2 threshold	[ 0 – 20000 ppm ]	12-2

Max infl. on liquid CO2 threshold	[ 0 – 20000 ppm ]	12-2

Wind speed for minimum influence	[ 0 – 72 km/h ]	12-2

Wind speed for maximum influence	[ 0 – 72 km/h ]	12-2

Max infl. on free CO2 threshold	[ 0 – 20000 ppm ]	12-2

Max infl. on forced CO2 threshold	[ 0 – 20000 ppm ]	12-2

Max infl. on liquid CO2 threshold	[ 0 – 20000 ppm ]	12-2

Vent position for min.  influence	[ 0 – 100 % ]	12-2

Vent position for max. influence	[ 0 – 100 % ]	12-2

Max infl. on free CO2 threshold	[ 0 – 20000 ppm ]	12-2

Max infl. on forced CO2 threshold	[ 0 – 20000 ppm ]	12-2

Max infl. on liquid CO2 threshold	[ 0 – 20000 ppm ]	12-2

12.2.2	Wind speed	12-2

12.2.3	Vent	12-2

12.2.4	Vent influences	12-2

CO2 level start influence	[ 0 – 20000 ppm ]	12-2

CO2 level maximum influence	[ 0 – 20000 ppm ]	12-2

Max infl on max vent pos,lee	[ 0 – 100 % ]	12-2

Max infl on max vent pos, wind	[ 0 – 100 % ]	12-2

CO2 influ. on max vent pos 	[ Yes / No ]	12-2

Max vent pos during inject.	[ 0 – 100 % ]	12-2

Time maintain max. vent position	[ 0 – 900 min ]	12-2

Min wind speed influence	[ 0 – 72 km/h ]	12-2

Max wind speed influence	[ 0 – 72 km/h ]	12-2

Max infl. on max pos, for CO2	[ 0 – 100 % ]	12-2

Max vent pos stops forced CO2	[ 0 – 100 % ]	12-2

Max  influ. vent pos max inj time	[ 0 – 100 % ]	12-2

Max infl. max inj. time, blr CO2 	[+/- 30000 sec]	12-2

Max infl. on max inj. time, liq. CO2	[+/- 30000 sec]	12-2

12.3	General Settings	12-3

Enable CO2 injections	[ Yes / No ]	12-3

Minimum injection time 	[ 0 – 1440 min ]	12-3

Delay before CO2 valve opens 	[ 0 – 1440 min ]	12-3

Maximum injection time 	[ 0 – 1440 min ]	12-3

Enable alarm (CO)	[ Yes / No ]	12-3

Pos valve liquid CO2 boiler ON	[ 0 – 100 % ]	12-3

Overall valve control time	[ 0 – 1200 sec ]	12-3

12.4	Configuration	12-3

CO2 measurement sample time	[ 0 – 1200 sec ]	12-3

PPM increase halts injections	[ 0 – 20000 ppm ]	12-3

No. comparts requesting CO2	[ 1 – n° compart ]	12-3

Boiler water T° increase	[ 0 – 100 % ]	12-3

13	FORCED AIR HEATING	13-1

13.1	Setting up control	13-1

Start temperature	[ -10/+40 °C ]	13-1

Stop temperature	[ -10/+40 °C ]	13-1

13.2	Configuration	13-1

Minimum ON time	[ 0 – 60 min ]	13-1

Minimum OFF time	[ 0 – 60 min ]	13-1

Forced air control T° input	[ 0 – 256 ]	13-1

Cooling	[ Yes / No ]	13-1

Temperature sensor	[ T1, T2,  T1/T2 ]	13-1

CO2 measurement sample time	[ 0 – 1200 sec ]	13-1

13.3	Influences	13-2

13.3.1	Solar radiation	13-2

Rad. for minimum influence	[ 0 – 1000 W/m² ]	13-2

Rad. for maximum influence	[ 0 – 1000 W/m² ]	13-2

Max influence on start/stop T°	[ -40/+40 °C]	13-2

Accumul. radiation start influ.	[0 -10000 Wh/m² ]	13-2

Accumul. radiation for max influ.	[0 -10000 Wh/m² ]	13-2

Max influence on start/stop T°	[ -40/+40 °C]	13-2

Time influence starts	[ 00:00 – 23:59 ]	13-2

Time influence ends	[ 00:00 – 23:59 ]	13-2

13.3.2	Assisted CO2 working	13-2

Enable forced air for CO2	[ Yes / No ]	13-2

Start time	[ 00:00 – 23:59 ]	13-2

End time	[ 00:00 – 23:59 ]	13-2

CO2 level start fan assist	[ 0 – 20000 ppm ]	13-2

CO2 level stops fan assist	[ 0 – 20000 ppm ]	13-2

CO2 level suspends heating	[ 0 – 20000 ppm ]	13-2

Maximum temperature	[ 0 – 50 °C ]	13-2

13.3.3	Humidity Influence	13-2

ON time	[ 0 – 60 min ]    ]	13-2

OFF time	[ 0 – 60 min ]	13-2

Maximum temperature	[ 0 – 130 °C ]	13-2

14	SCREENS	14-1

14.1	Time based control	14-1

Operate at fixed times	[ Yes / No ]	14-1

Time screen unfolds, per 1	[ 00:00 – 23:59 ]	14-1

Time screen folds, per 1	[ 00:00 – 23:59 ]	14-1

Time screen unfolds, per 2	[ 00:00 – 23:59 ]	14-1

Time screen folds, per 2	[ 00:00 – 23:59 ]	14-1

Maximum length of screen	[ 0 – 1000 cm ]	14-1

Max permitted humidity	[ 0 – 100 % ]	14-1

Max permitted temperature	[ -40/+40 °C]	14-1

Fold, humidity exceeds max	[ 0 – 1000 cm/% ]	14-1

Fold, temperature exceeds max.	[ 0 – 1000 cm/% ]	14-1

Limit folding due to T and RH	[ 0 – 1000 cm ]	14-1

Rad. cancels influ. T and RH	[ 0 – 1000 W/m² ]	14-1

Start time	[ 00h00 – 23h59 ]	14-1

End time	[ 00h00 – 23h59 ]	14-1

O/s T° folds screen (thermal)	[ -25/+40 °C ]	14-1

14.2	Shading control	14-1

Operate screen for shading	[ Yes / No ]	14-1

Time screen unfolds	[ 00:00 – 23:59 ]	14-1

Time screen folds	[ 00:00 – 23:59 ]	14-1

Radiation, shade length 1	[ 0 – 1000 W/m² ]	14-1

Shade length 1	[ 0 – 1000 cm ]	14-1

Radiation, shade length 2	[ 0 – 1000 W/m² ]	14-1

Shade length 2	[ 0 – 1000 cm ]	14-1

Radiation level folds screen	[ 0 – 1000 W/m² ]	14-1

Shade control folding delay	[   ]	14-1

Max permitted humidity	[ 0 – 100 % ]	14-1

Max permitted temperature	[ -40/+40 °C]	14-1

Fold, humidity exceeds max	[ 0 – 1000 cm/% ]	14-1

Fold, temperature exceeds max	[ 0 – 1000 cm/°C ]	14-1

Limit folding due to T and RH	[ 0 – 1000 cm ]	14-1

14.3	Thermal Operation	14-2

Thermal screen control	[ Yes / No ]	14-2

Start thermal period, night	[ 00:00 – 23:59 ]	14-2

O/s T unfolds screen, night	[ -25/+40 °C ]	14-2

Maximum length	[ 0 – 1000 cm ]	14-2

Time end thermal period	[ 00:00 – 23:59 ]	14-2

O/s T folds screen, day	[ -25/+40 °C ]	14-2

Radiation level folds screen	[ 0 – 1000 W/m² ]	14-2

Daytime rad. unfolds screen	[ 0 – 1000 W/m² ]	14-2

Daytime amb. T unfolds screen	[ -40/+40 °C]	14-2

Max permitted humidity	[ 0 – 100 % ]	14-2

Max permitted temperature	[ -40/+40 °C]	14-2

Fold, humidity exceeds max	[ 0 – 1000 cm ]	14-2

Fold, temperature exceeds max	[ 0 – 1000 cm ]	14-2

Limit folding due to T and RH	[ 0 – 1000 cm ]	14-2

Initial fold control distance	[ 0 – 1000 cm ]	14-2

Folding % increase per step	[ 0 – 100 % ]	14-2

Start normal folding at	[ 0 – 1000 cm ]	14-2

Fold if snow detected	[ Yes / No ]	14-2

Max inf on outside T°, unfolding	[ -10/+40 °C ]	14-2

Max inf on outside T°, folding	[ -10/+40 °C ]	14-2

Type of ambient T°	[ 0, 1 ]	14-2

14.4	Influences On Thermal Screen Folding	14-3

14.4.1	Wind speed	14-3

Wind speed for min influence	[ 0 – 72 km/h ]	14-3

Wind speed for max influence	[ 0 – 72 km/h ]	14-3

Influence on control interval	[ 0 – 120 min ]	14-3

Influence on % folding	[ 0 – 100 % ]	14-3

Reduction limit folding max T/H	[ 0 – 1000 cm ]	14-3

Outside T for min influence	[ -25/+40 °C ]	14-3

Outside T for max influence	[ -25/+40 °C ]	14-3

Influence on control interval	[ 0 – 120 min ]	14-3

Influence on %  folding 	[ 0 – 100 % ]	14-3

Reduction limit  folding max T/H	[ 0 – 1000 cm ]	14-3

Htg T diff. for min influence	[ -10/+20 °C ]	14-3

Htg T diff. for max influence	[ -10/+20 °C ]	14-3

Influence on control interval	[ 0 – 120 min ]	14-3

Influence on %  folding 	[ 0 – 100 % ]	14-3

14.4.2	Outside temperature	14-3

14.4.3	Heating	14-3

14.5	Thermal Screen Influence On Heating Set-point	14-3

Infl. on htg water T, unfold	[ -90/+90 °C ]	14-3

Infl. on htg water T, fold	[ -90/+90 °C ]	14-3

Influence on heating 1	[ Yes / No ]	14-3

Influence on heating 2	[ Yes / No ]	14-3

Influence on heating 3	[ Yes / No ]	14-3

14.6	General Settings	14-4

Screen control interval	[ 0 – 120 min ]	14-4

Minimum correction length	[ 0 – 1000 cm ]	14-4

Maximum correction length	[ 0 – 1000 cm ]	14-4

Max variation, plus	[ 0 – 1000 W/m² ]	14-4

Max variation, minus	[ 0 – 1000 W/m² ]	14-4

14.7	Configuring The Screen	14-4

Control time to fold	[ 0 – 1800 sec ]	14-4

Control, time to unfold	[ 0 – 1800 sec ]	14-4

Control folding distance	[ 0 – 1000 cm ]	14-4

Control motor delay	[    sec ]	14-4

Minimum length, rain detected	[ 0 – 1000 cm ]	14-4

Minimum length, storm detected	[ 0 – 1000 cm ]	14-4

No of screen to track (master)	[ 1 – n° comp. ]	14-4

Comp number of master screen	[ 1 – n° comp. ]	14-4

Track light in compartment n°	[ 1 – n° comp.]	14-4

Time after end stop	[ 0 – 300 sec ]	14-4

Minimum positional control	[ 0 – 2000 ms ]	14-4

Alarm delay	[ 0 – 1440 sec ]	14-4

15	CIRCULATION FAN	15-1

15.1	Setting Up Control	15-1

Enable fan operation	[ Yes / No ]	15-1

Temp. difference starts fan	[ 0 – 40 °C ]	15-1

Humidity diff. starts fan	[ 0 – 50 % ]	15-1

Heating water T starts fan	[ 0 – 130 °C ]	15-1

Start cyclic fan operation	[ 0 – 1440 min ]	15-1

ON time, cyclic operation	[ 0 – 1440 min ]	15-1

Minimum ON time	[ 0 – 1440 min ]	15-1

Maximum ON time	[ 0 – 1440 min ]	15-1

Minimum OFF (pause) time	[ 0 – 1440 min ]	15-1

Vent position stops fan	[ 0 – 100 % ]	15-1

CO2 level starts fan	[ 0 – 20000 ppm ]	15-1

CO2 Injection starts fan	[ Yes / No ]	15-1

Minimum vent position	[ 0 – 100 % ]	15-1

16	VENTILATION  FAN	16-1

16.1	Setting up control	16-1

Enable fan operation	[ Yes / No ]	16-1

Start time	[ 00:00 – 23:59 ]	16-1

End time	[ 00:00 – 23:59 ]	16-1

Deficit starts fan	[ -50 / +50 mBar ]	16-1

Ventilation T° diff. starts fan	[ 0 – 50 ]	16-1

CO2 level starts fan	[ 0 – 20000 ppm ]	16-1

Minimum ON time	[ 0 – 1440 min ]	16-1

Minimum OFF (pause) time	[ 0 – 1440 min ]	16-1

Maximum ON time	[ 0 – 1440 min ]	16-1

Maximum vent position	[ -100 / +100 % ]	16-1

Minimum vent position	[ 0 – 100 % ]	16-1

Minimum outside deficit	[ 0 – 50 mBar ]	16-1

Maximum outside deficit	[ 0 – 50 mBar ]	16-1

Deficit triggers aux output	[ 0 – 50 mBar ]	16-1

Temp triggers aux output	[ 0 – 50 °C ]	16-1

Number of auxiliary output	[ 0 – 256 ]	16-1

Compartment number for vents	[ 1 – no comp. ]	16-1

Number of vent	[ 1 –  8 ]	16-1

17	LIGHTING	17-1

17.1	Setting up cyclic control	17-1

Enable lighting cycle	[ Yes / No ]	17-1

Period 1 starts	[ 00:00 – 23:59 ]	17-1

Lighting ON time	[ 0 – 1200 min ]	17-1

Lighting OFF (pause) time	[ 0 – 1200 min ]	17-1

Period 1 ends	[ 00:00 – 23:59 ]	17-1

Period 2 starts	[ 00:00 – 23:59 ]	17-1

Lighting ON time	[ 0 – 1200 min ]	17-1

Lighting OFF (pause) time	[ 0 – 1200 min ]	17-1

Time cyclic ends	[ 00:00 – 23:59 ]	17-1

Rad. activates lighting	[ 0 – 1000 W/m² ]	17-1

Rad. deactivates lighting	[ 0 – 1000 W/m² ]	17-1

Amb. temp. deactiv. lighting	[ 0 – 40 °C ]	17-1

Enable cascade lighting 	[ Yes / No ]	17-1

17.2	Assimilation Lighting	17-1

Enable lighting	[ Yes / No ]	17-1

Start time	[ 00:00 – 23:59 ]	17-1

Radiation activates lighting	[ 0 – 1000 W/m² ]	17-1

Radiation deactivates lighting	[ 0 – 1000 W/m² ]	17-1

Minimum ON time	[ 0 – 1440 min ]	17-1

Minimum OFF (pause) time	[ 0 – 1440 min ]	17-1

Max permitted temperature	[ 0 – 40 °C ]	17-1

End time	[ 00:00 – 23:59 ]	17-1

Interval between lighting ctl	[ 0 – 1440 min ]	17-1

Light assimilation set-point	[ 0– 20000Wh/m²]	17-1

Time end accumul. radiation	[ 00:00 – 23:59 ]	17-1

Theoretical W/m2 figure	[ 0 – 1000 W/m² ]	17-1

Amb. temp diff. lighting ON	[ -40/+40 °C]	17-1

Amb. temp diff. lighting OFF	[ -40/+40 °C]	17-1

Lighting OFF delay 	[  ]	17-1

Lighting ON delay	[  ]	17-1

Sensor type	[ 0,1 ]	17-1

18	ROOF SPRINKLERS	18-1

18.1	Setting up control	18-1

Enable roof sprinklers	[ Yes / No ]	18-1

Start time	[ 00:00 – 23:59 ]	18-1

End time	[ 00:00 – 23:59 ]	18-1

ON time	[ 0 – 1200 min ]	18-1

OFF time	[ 0 – 1200 min ]	18-1

Amb. T° start sprinklers	[ 0 – 40 °C ]	18-1

Deficit start sprinklers	[ 0 – 50 mBar ]	18-1

Radiation enable sprinklers	[ 0 – 1000 W/m² ]	18-1

Max vent pos sprinklers ON	[ 0 – 100 % ]	18-1

Wind speed stop sprinklers	[ 0 – 72 km/h ]	18-1

Stop if rain detected	[ Yes / No ]	18-1

Start if frost detected	[ Yes / No ]	18-1

Number of compartment to follow	[ 1 – n° comps ]	18-1

19	FOG SYSTEM	19-1

19.1	Setting up control	19-1

Enable fog system	[ Yes / No ]	19-1

Start time	[ 00:00 – 23:59 ]	19-1

End time	[ 00:00 – 23:59 ]	19-1

Fog ON time	[ 0 – 30000 sec ]	19-1

Fog OFF time	[ 0 – 30000 sec ]	19-1

Deficit starts fog	[ 0 – 50 mBar ]	19-1

Max deficit stops fog	[ 0 – 50 mBar ]	19-1

Temperature starts fog	[ 0 – 40 °C ]	19-1

Max pos vent allow fogging	[ 0 – 100 % ]	19-1

Max vent pos with fogging ON	[ 0 – 100 % ]	19-1

Time max wind influ. fog ON time	[ +/- 1000 sec ]	19-1

Radiation start influence	[ 0 – 1000 W/m² ]	19-1

Radiation max influence	[ 0 – 1000 W/m² ]	19-1

Time max rad. influ. OFF time	[ +/- 1000 sec ]	19-1

Fog cascade working	[ Yes / No ]	19-1

Humidity starts fog	[ 0 – 100 % ]	19-1

Humidity stops fog	[ 0 – 100 % ]	19-1

Type of ambient T°	[ 0, 1 ]	19-1

Min time maintain vent position	[ 0 – 1440 min ]	19-1

20	FUMIGATION TREATMENT PERIOD	20-1

20.1	Setting up control	20-1

Enable phytosan. treatment	[ Yes / No ]	20-1

Fix treatment date	[ Yes / No ]	20-1

Treatment date	[ DD/MM/YY ]	20-1

Start time	[ 00:00 – 23:59 ]	20-1

End time	[ 00:00 – 23:59 ]	20-1

Vent pos during treatment	[ 0 – 100 % ]	20-1

Min vent pos after treatment	[ 0 – 100 % ]	20-1

Time min pos after treatment	[ 0 / 1440 min ]	20-1

Max vent pos after treatment	[ 0 – 100 % ]	20-1

Time max pos after treatment	[ 0 / 1440 min ]	20-1

Heating min water temp increase	[ -130 / +100 °C ]	20-1

Max temperature permit treatment	[ 0 – 50 °C ]	20-1

Max pos vent if temp exceeds max	[ 0 – 100 % ]	20-1

Activate phytosan. o/p	[ Yes / No ]	20-1

Output activation time	[ 0 / 1440 min ]	20-1

Pause between during and after	[ 0 / 1440 min ]	20-1

20.1.1	Circulation fan operation	20-1

Enable fan for phyto.	[ Yes / No ]	20-1

Fan ON time during treatment	[   min ]	20-1

Fan ON time after treatment	[   min ]	20-1

Stop fan during	[ Yes / No ]	20-1

Fan Pause time after treatment	[   min ]	20-1

Fan ON time before treatment	[   min ]	20-1

20.1.2	Screen operation	20-2

Scr. length during treatment	[ 0 / 1000 cm ]	20-2

Scr. length after treatment	[ 0 / 1000 cm ]	20-2

Time screen after treatment	[ 0 / 1440 min ]	20-2

20.2	Summary	20-2

21	GROUND COOLING	21-1

21.1	Setting up control	21-1

Enable ground cooling	[ Yes / No ]	21-1

Start time	[ 00:00 / 23:59 ]	21-1

End time	[ 00:00 / 23:59 ]	21-1

Minimum water temperature	[ 0 – 30 °C ]	21-1

Maximum water temperature	[ 0 – 30 °C ]	21-1

Delay bef. stop GC, if max wtr T°	[ 0 – 1440 min ]	21-1

Start temperature	[ -25/+40 °C ]	21-1

Stop temperature difference	[ -25/+40 °C ]	21-1

3WV control time per °C	[ 0 – 120 sec ]	21-1

Max variation V3V per interval	[ 0 – 100 % ]	21-1

21.2	Configuration	21-2

3WV position start ground cooling	[ 1 – 100% ]	21-2

Minimum ON time	[ 0 – 1439 min ]	21-2

Modulate heating 3WV	[ Yes / No ]	21-2

21.2.1	Reference temperatures if ground cooling enabled	21-2

22	AUXILIARY PERIOD	22-1

22.1	Setting up control	22-1

Enable auxiliary period	[ Yes / No ]	22-1

Start time	[ 00:00 / 23:59 ]	22-1

End time	[ 00:00 / 23:59 ]	22-1

Transition time at start	[ 0 – 120 min ]	22-1

Transition time at end	[ 0 – 120 min ]	22-1

Influence on leeward ventilation T°	[ -50/+50 °C]	22-1

Influence on leeward vent min pos	[ -100/+100 % ]	22-1

Influence on windward ventil. T°	[ -50/+50 °C]	22-1

Influence on windward vent min pos	[ -100 /+100 % ]	22-1

Influence on T°, heating 1	[ -50/+50 °C ]	22-1

Influence on min wtr T°, heating 1	[ -100/+100 °C ]	22-1

Influence on T°, heating 2	[ -50/+50 °C ]	22-1

Influence on min wtr T°, heating 2	[ -50/+50 °C ]	22-1

23	AIR INFLATED WALLS	23-1

23.1	Setting up control	23-1

Activate air inflation	[ Yes / No ]	23-1

Start time	[ 00:00 / 23:59 ]	23-1

End time	[ 00:00 / 23:59 ]	23-1

ON time	[ 0 – 1440 sec ]	23-1

OFF (pause) time	[ 0 – 500 min ]	23-1

Wind speed for min influence	[ 0 – 100 km/h ]	23-1

Wind speed for max influence	[ 0 – 100 km/h ]	23-1

Maximum influence ON time	[ 0 – 100 sec ]	23-1

Maximum influence OFF time	[ 0 – 100 min ]	23-1

24	TEMPERATURE INTEGRATION	24-1

24.1	Setting up control	24-1

Enable temperature integration	[ Yes / No ]	24-1

Start time	[ 00:00 / 23:59 ]	24-1

End time	[ 00:00 / 23:59 ]	24-1

Average temp. (integration steps)	[ -50/+50 °C ]	24-1

Inf. per degree difference	[ -50/+50 °C ]	24-1

Max inf. on ventilation temperature	[ -50/+50 °C ]	24-1

Max inf. on ambient temperature	[ -50/+50 °C ]	24-1

Transition (slope) time at start	[ 0 / 1440 min ]	24-1

Transition (slope) time at end	[ 0 / 1440 min ]	24-1

Number of integration steps	[ 1 / 72 ]	24-1

25	MISCELLANEOUS FUNCTIONS	25-1

25.1	How to Copy the Contents of Menus	25-1

25.2	Printouts	25-1

Printout compartment	[ 1 – n° compart ]	25-1

Printout all compartments	[ Yes / No ]	25-1

Heating	[ Yes / No ]	25-1

Vents	[ Yes / No ]	25-1

Humidity	[ Yes / No ]	25-1

Screens 	[ Yes / No ]	25-1

Periods	[ Yes / No ]	25-1

Fog system	[ Yes / No ]	25-1

Circulation fan	[ Yes / No ]	25-1

Lighting	[ Yes / No ]	25-1

CO2	[ Yes / No ]	25-1

Alarms	[ Yes / No ]	25-1

Boiler	[ Yes / No ]	25-1

Weather Station	[ Yes / No ]	25-1

25.2.1	Averages	25-1

Printout compartment	[ 1 – n° compart ]	25-1

Printout all compartments	[ Yes / no ]	25-1

Printout the averages	[ Yes / no ]	25-1

Printout averages daily	[ Yes / no ]	25-1

# INTRODUCTION

- Control panel features.

- Power-up and installed program details.

LCD display

Keys F1 to F5

Numeric keypad

Misc. keys

8

7

9

4

5

6

1

2

3

-

0

.









A















Direction

arrows

Control Panel

- The LCD display provides access to all readings and programming information through a structured system of menus.

- The five function keys - F1 to F5 – correspond to the menu option fields at the bottom of the display: use these keys for navigating through the menu system.

- The four direction arrows allow line scrolling and moving between fields in the display.

- The numeric keypad is used for number, dash and dot entry, as appropriate.

- The three Misc. keys are used for:

entry of alphabetic characters (A to Z), short cut to Alarms menu

A

backspace deleting the last character entered



copy / pasting between identical menus.



## Power Up Display (Global)

| Current date M.C.U. Global |  |  |  |  |  |  |  |  |  | 00 : 00 : 00 |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Date : 24/03/03 Initialization : H.OK DG1 Last shutdown : 24/03/03 15:30 |  |  |  |  |  |  |  |  |  |  |  |
| VER |  |  |  |  |  |  |  |  | O K |  |  |

- Initialization:

H.OK = good internal battery,

DGn = dongle (software protection key), where	n = -1 for dongle not detected (inhibits the program)

=  0 for PC connection not included

=  1 for PC connection included

=  2 & 3 for Ferti program options.

- Date and time of last shutdown (or power loss).

- VER     displays brief program details.

- O K      returns to the main menu.

## Installed Program Details (Global)

POWER UP   VER

| Program number. M.C.U. Global |  |  |  |  |  |  |  |  |  | 00 : 00 : 00 |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Prog num.: 1154/02 Key num : C3.1154 Ferti : version 6.03a 2st:4Ve:0ar/12G/30V/0A/6C/1P Climat : version 5.04a 3Cpt/1Tpt/3Blr/0Inp |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  | QUIT |  |  |

- Protection key number.

- The configuration line (Climat): contains the version number together with the number of:

compartments (C),

transports (Tpt),

boilers (Blr), and

auxiliary inputs (Inp).

- QUIT      :	go back to power up menu.

Main Menu

POWER UP   O  K    RIGHT DIRECTION ARROW

| M.C.U. Global |  |  |  |  |  |  |  |  |  | 00 : 00 : 00 |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ALARMS |  | READOUT |  | GENERAL |  | COMPART |  |  | SYSTEM |  |  |

- ALARMS   :	view history of alarms, cancel alarm for 1 minute, set alarm thresholds.

- READOUT:	view status readings for the main climate control systems.

- GENERAL :	program configuration settings for the weather monitoring station and common  heating equipment, that			is boiler, transports, storage tank, CO2.

Note: requires access level 3 (PROGRAM) permission.

- COMPART:	program settings for individual compartments.

Note: dependant on access level.

- SYSTEM  :	set up access permissions for users, program the installation parameters.

Note: requires access at the higher (INSTAL) levels.

## Menu tree outline

Boxed menu options denote chapters in this guide (see Contents).

ALARMS

READOUT

GENERAL

COMPART

SYSTEM

HISTORY / RESET / STOP / MODIFY (thresholds)

OTHER

MORE

AVERAGE

VENTS

HEATING

BOILER

RAIN (pluvio.)

OTHER (inf. on wind vane meas.)

HEATING

BLR CFG

FIRING

VARIOUS

OST INF

WND INF

RAD INF

HUMIDTY

TPT CFG

CFG CO2

INFLUE

GENERAL

SYNCHRO

SAFETY

OST INF

WND INF

RAD INF

FOG

CFG VNT

WIND VA

(compart. orient.)

BOILER

INFLUE

CFG HTG

SAFETY

FCD AIR

RAD INF

CO2 INF

HUM INF

CONFIG

FAN (exhaust)

NEXT (assim.)

FAN INF

SCR  INF

Key ‘1’

SPRINKL

AIR-INFL. WALLS

TEMP. INTEGRATION

OTHER

PRINT

HEATING

OTHER

OTHER

OTHER

OTHER

OTHER

OTHER

TRANSPT

CO2

CO2

RAD INF

VNT INF

OTHER

THERMAL

FIX TIM

SHADE

VARIOUS

SCREENS

INFLUE

OTHER (htg)

GENERAL

CFG SCR

COOLING (ground)

PERIODS

FAN  (circ.)

OTHER

LIGHTING

PHYTO (fumig.)

AUX PER

MAIN MENU BAR

BLR=boiler;     CFG=configuration;

FCD=forced;     HTG=heating;      HUM=humidity;     INF=influence;      OST= outside t°;     RAD= solar radiation;    PER=period;      SCR= screen;       TIM=time;     TPT=transport;       VA= vane;     VNT=vent;      WND=wind;

Key ‘2’

CODE

(access /install.)

VENTS

MODIFY (mode)

VNT CTL (regul.)

HTG CTL (regul.)

WEATHER

# DAY-TO-DAY MONITORING

- Compartment environment (T°, RH, Saturation Deficit).

- Environmental averages (inside and outside).

- Vents and heating – status and influences.

- Boiler status.

### T°, RH and Vents

MAIN MENU  READOUT

| Compartment 1 Period 2 |  |  |  |  |  |  |  |  | 10 : 12 : 15 |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Temp Humi Def WIND LEE |  |  |  |  |  |  |  |  |  |  |
| Meas 19.5 75 5.7 0 15 Ctrl 18.0 0 15 Max 87 6.0 30 80 Min 73 3.0 0 0 |  |  |  |  |  |  |  |  |  |  |
| COMPART |  | MORE |  | WEATHER |  | OTHER |  |  |  | QUIT |

Rows

- Meas	= current reading.

- Ctrl	= calculated set-point.

- Min /Max	= calculated min /max set-points (but user saturation deficit set-points).

Note: vent set-points include influences. The SYNCHRO message appears above the columns when synchronization of the vents occurs.

Columns

- Temp	= ambient temperature (but ventilation temperature set-point).

- Humi	= ambient RH.

Note: max and min thresholds are based on the saturation deficit set-points and the ambient temperature measurement (see Humidity Control for an explanation).

- Def		= saturation deficit.

- LEE / WIND	= status of lee and windward vents.

Note: column 1 corresponds to vent 1, column 2 to vent 2, but the LEE and WIND labels change to match the wind direction.

- COMPART  :	= next compartment display.

- WEATHER :	= view outside climatic conditions.

- OTHER     :	= view environmental averages, and influences on vents and heating.

### Heating

MAIN MENU  READOUT  MORE

| Compartment 1 Period 2 |  |  |  |  |  |  |  |  | 10 : 12 : 15 |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Htg 1 temp. |  |  |  |  |  |  |  |  |  |  |
| Temp Humi Def Wtr Trpt Blr |  |  |  |  |  |  |  |  |  |  |
| Meas 19.5 75 5.7 32.0 36.5 65.0 Ctrl 16.0 30.0 35.0 70.0 Max 87 6.0 60.0 65.0 85.0 Min 73 3.0 30.0 35.0 70.0 |  |  |  |  |  |  |  |  |  |  |
| COMPART |  | MORE |  | WEATHER |  | OTHER |  |  |  | QUIT |

Columns

- Temp	= ambient temperature and set-point.

- Wtr	= heating water temperature.

- Trpt	= transport water temperature.

- Blr	= boiler water temperature.

- Htg. 1 temp	= denotes primary heating circuit.

- Htg. 2 temp	= denotes secondary heating circuit (overhead, grow or low-level).

- MORE       	= view more information.

MAIN MENU  READOUT  MORE

| Compartment 1 Period 2 |  |  |  |  |  |  |  |  | 10 : 12 : 15 |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Ground htg |  |  |  |  |  |  |  |  |  |  |
| Temp Humi Def Wtr Trpt Blr Gnd |  |  |  |  |  |  |  |  |  |  |
| Meas 19.5 75 5.7 21.0 26.5 65.0 21.5 Ctrl 20.0 25.0 70.0 19.0 Max 87 6.0 40.0 45.0 85.0 Min 73 3.0 30.0 25.0 70.0 |  |  |  |  |  |  |  |  |  |  |
| COMPART |  | MORE |  | WEATHER |  | OTHER |  |  |  | QUIT |

Columns

As per previous menu

+

- Gnd	= current values for the ground or substrate medium.

- COMPART  	= next compartment display.

- WEATHER 	= view outside environmental conditions.

- OTHER     	= view environmental averages, and influences on vents and heating.

### Averages

READOUT    OTHER  AVERAGE

| The average, maximum and minimum values can be displayed for the last four compartment periods. The outside environmental averages are always based on the compartment 1 periods. Averages readout comp 1 |  |  |  |  |  |  |  |  | 10 : 12 : 15 |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Period 05:53R / 18:00S (2) |  |  |  |  |  |  |  |  |  |  |
| Temp Humi Gnd o/sT° o/sRH Rad Wind |  |  |  |  |  |  |  |  |  |  |
| Avg 19.5 75 16.4 12.0 68 214 7 Max 25.0 80 18.6 20.0 72 400 12 Min 17.6 65 15.5 8.0 53 50 0 |  |  |  |  |  |  |  |  |  |  |
| COMPART |  | PERIOD |  | MORE |  | NIGHT/DAY |  |  |  | QUIT |

Columns

- Temp	= ambient temperature (C).

- Humi	= ambient relative humidity (%)

- Gnd	= ground (substrate) temperature (C).

- o/s T	= outside temperature (C).

- o/sRH	= outside relative humidity (%).

- Rad	= instantaneous solar radiation (W/m²).

- Wind	= wind speed (Km/h).

- Vent 1 & 2 	= positions of vents 1 and 2 (%).

- MORE       	= view vent and boiler averages   .

- NIGHT/DAY  	= change between current day/night period and previous night/day period (then ‘QUIT’ to return).

- PERIOD    	= next period.

### Influences On Vents

READOUT    OTHER    VENTS

| Influences on vent comp 1 |  |  |  |  |  |  |  |  | 10 : 12 : 15 |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Vent Temp Humi SAFE o/sTI WspI RadI Ctrl |  |  |  |  |  |  |  |  |  |  |
| WIND 15 0 NO 0 10 0 13 LEE 40 0 NO 0 10 0 36 |  |  |  |  |  |  |  |  |  |  |
| COMPART |  | MORE |  | SYNCHRO |  |  |  |  |  | QUIT |

Columns

- Temp	= position based on temperature alone.

- Humi 	= position based on humidity alone.

- SAFE	= safety position (rain, storm, frost, fogging, ventilation, none).

- osTI	= percentage of outside temperature influence.

- WspI 	= percentage of wind speed influence.

- RadI	= percentage of instantaneous sunlight intensity influence.

- Ctrl	= final set-point position.

- MORE       	= view more information, as follows.

- Calc 	= position based on temperature and humidity.

- TRND	= current value of trend % correction to be applied at start of next control cycle .

- Meas	= vent position measurement if sensor fitted.

- SYNCHRO 	= force synchronization of vents for current or all compartments.

### Influences On Heating

READOUT    OTHER   HEATING

| Heating details comp 1 |  |  |  |  |  |  |  |  | 10 : 12 : 15 |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Htg Ctrl CO2I RHI AcRI RadI o/sTI WspI |  |  |  |  |  |  |  |  |  |  |
| 1 50.0 0 100 0 0 0 0 2 25.0 0 0 0 0 0 0 3 20.0 0 0 0 0 0 0 |  |  |  |  |  |  |  |  |  |  |
| COMPART |  | MORE |  | TRANSPT |  | BOILER |  |  |  | QUIT |

Columns

- Htg	= heating systems 1, 2, & 3  (primary, secondary, & ground).

- Ctrl	= heater water set-point temperature.

- CO2I	= percentage of CO2 influence.

- RH I	= percentage of humidity influence during dehumidification (drying).

- AcRI	= percentage of accumulated radiation influence during evening period.

- osTI	= percentage of outside temperature influence.

- WspI	= percentage of wind speed influence.

- RadI	= percentage of instantaneous solar radiation influence.

- MORE       	= view more information, as follows.

- 3WV 	= position of heating loop 3-way mixing valve.

- PUMP	= status of the heating loop pump.

- Meas	= heating water temperature measurement.

- Rtrn	= heating water return temperature measurement.

- TRANSPT   	= view transport line information.

- BOILER      	= view boiler information.

### Boiler Status

READOUT    OTHER   HEATING.  BOILER

| Boiler details |  |  |  |  |  |  |  |  | 10 : 12 : 15 |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Water temperature |  |  |  |  |  |  |  |  |  |  |
| Blr Stus Ctrl Time Meas Rtrn |  |  |  |  |  |  |  |  |  |  |
| 1 STOP 70.0 10 65.0 63.0 |  |  |  |  |  |  |  |  |  |  |
|  |  | MORE |  |  |  |  |  |  |  | QUIT |

Columns

- Blr	= boiler number.

- Stus	= status, which can be:											STOP	= not in service											YES	= ON 												NO	= OFF 												3WV	= forced opening of supplied heating and transport mixing valves.

- Ctrl 	= boiler water temperature set-point.

- Time	= ON time since back in service.

- Meas	= boiler water temperature measurement.

- Rtrn	= boiler return water temperature measurement.

- MORE       	= view more information, as follows.

- Burn 	= position of burner valve if modulated.

- CO2I	= percentage of CO2 influence.

# ALARMS

- Current and logged alarms (history).

- Temporary disabling.

- Setting thresholds and delay.

## Readings

ALARM

| Columns Current alarms |  |  |  |  |  |  |  |  | 10 : 12 : 15 |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Start End Type N° Date |  |  |  |  |  |  |  |  |  |  |
| A 04:32 04:32 Alarm max temperature 04 06/04/2003 |  |  |  |  |  |  |  |  |  |  |
| HISTORY |  | RESET |  | STOP |  | MODIFY |  |  |  | QUIT |

- Alarms are identified by the letter ‘A’ on the left of the menu.

- Start: indicates the time the alarm was detected.

- End: for stored alarms this indicates the time when the alarm conditions disappeared, and for an active alarm it shows the current time.

- Type: provides a description of the alarm (see below for the list).

- N°: identifies the compartment (or input) generating the alarm.

- Date: identifies the date of the alarm.

Management

Press HISTORY   to display the last 10 stored alarms.

Press   RESET     to clear the stored alarms list.

Press    STOP    to silence the buzzer and turn OFF the MCU alarm output for 1 minute. This causes the alarm history to display and the key function to change to   START , re-enabling the buzzer (an audible signal emitted at regular intervals). Press  MODIFY   to work with alarm thresholds.

List of alarm types

- Min compart T°	= low ambient temperature.

- Max compart T°	= low ambient temperature.

- Min compart humidity	= low relative humidity.

- Max compart humidity	= high relative humidity.

- Min ground T°		= low ground temperature.

- Max ground T°	= high ground temperature.

- Min CO2 level	= low CO2 concentration.

- Max CO2 level	= high CO2 concentration

- Vent alarm		= position exceeds tolerance (requires a sensor).

- Screen alarm	= position exceeds tolerance (requires a sensor).

- Heating "n" alarm	= difference between heating water measurement and set-point  temperatures exceeds ‘Water T° diff.			 triggers alarm’.

- Minimum boiler T°	= low boiler water temperature.

- Maximum boiler T°	= high boiler water temperature.

- CO injection alarm	= CO from boiler is detected (requires a dedicated input).

- Min boiler return T°	= low boiler return water temperature (requires a sensor).

- Max boiler return T°	= high boiler return water temperature (requires a sensor).

- Extra boiler T° input	= input level falls below threshold.

- Min input alarm	= low input level (outside expected range).

- Max input alarm	= high input level (outside expected range).

- PIA alarm		= program I/O control fault detected: alarm is immediate and affects all equipment controlled by 				the MCU.

Note: the only way to clear an alarm is by correcting the cause or by reprogramming the activation threshold(s) where appropriate.

## Activation Thresholds

ALARMS  MODIFY

| Alarm settings comp 1 |  |  |  |  |  |  |  |  |  | 10 : 12 : 15 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Enable compartment alarms [ Yes / No ] Minimum compart temperature [ -10/+40 °C ] Maximum compart temperature [ -10/+40 °C ] Max T increase at max radiation [ -10/+40 °C ] Minimum compartment humidity [ 0 – 100 % ] Maximum compartment humidity [ 0 – 100 % ] Minimum ground temperature [ -10/+40 °C ] Maximum ground temperature [ -10/+40 °C ] Min CO2 level activate alarm [ 0 – 20000 ppm ] Max CO2 level activate alarm [ 0 – 20000 ppm ] Alarm time delay [ 0 – 1440 min ] |  |  |  |  |  |  | : : : : : : : : : : : | YES 12.0 30.0 5.0 50 98 15.0 25.0 200 2000 10 |  |  |  | °C °C °C % % °C °C ppm ppm min |
|  |  |  |  |  |  | MODIFY |  |  |  |  | QUIT |  |

- Enable alarms for the compartment and set appropriate activation thresholds for ambient temperature, humidity, ground temperature and CO2 concentration.

- The ‘Max T° increase at max radiation’ setting increases the alarm threshold on maximum temperature when solar radiation reaches the theoretical daily maximum, which is based on geographical location.

- ‘Alarm time delay’: set a workable time delay before alarms annunciate in order to avoid the occurrence of spurious alarms.

CAUTION

Setting any threshold to ‘0’ disables the alarm.

# ACCESS CODES

- Three levels for day-to-day operation; three levels for commissioning and maintenance.

- Password setting to control access.

## Levels

Each successive level of access includes the permissions of the lower levels.

Operational

- READOUT: allows display of user set-points (e.g. ambient /ventilation T°), compartment readings, calculated set-points and alarms.

Note: programming settings is not possible, and a password is not required.

- RAPID:  allows modification of the basic settings for temperature, vents and heating, and displays enhanced readouts including influences.

- PROGRAM: allows all user operational settings to be programmed (influences, boiler,...).

Installation, commissioning and maintenance

- INSTAL1: allows modifications to and readings of the Kp, Ki, and Kd vent coefficients, heating systems, boiler(s) and transport(s), and provides the    INIT     key for initialization of the system, which includes all lower level passwords.

- INSTAL2: provides a readout of the identifiers that configure the system.

- INSTAL3: provides access to the  Start/Stop keys affecting measurement acquisition and regulation when making changes to the system identifiers.

## Setting up control

SYSTEM   CODE

| Press LEVEL to cycle through the access levels. Change level RAPID |  |  |  |  |  |  |  |  |  | 10 : 12 : 15 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Password Access level |  |  |  |  |  |  | : : | RAPID |  |  |  |  |
|  |  |  |  | LEVEL |  | O K |  |  |  |  | QUIT |  |

- Enter a password of up to 3 numeric characters (including "-" or "." if desired).

- Pressing   O K   to confirm means that an incorrect password will block access from now on (the display returns to ‘Readout’).

NOTE

Initially, simply pressing     O K      allows access to ALL levels.

CAUTION

Avoid day-to-day running at the INSTAL levels, since even minor operational errors can have potentially serious consequences.  User passwords are NOT set when the system is first installed, making all levels accessible. Similarly, if the system is reinitialized ALL passwords will be erased.

Changing passwords

Log on with the correct password and then press CHANGE (now visible) to enter and confirm the new password.

# PERIODS

- Period 1 = Restart; Period 2 = Day; Period 3 = Evening; Period 4 = Night.

- Clock or sunrise / sunset times.

- Transition times for gradual changeover between periods.

## Setting up control

COMPART  OTHER   PERIOD

| Columns Period settings comp 1 |  |  |  |  |  |  |  |  | 10 : 12 : 15 |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Period Time Sunrise Sunset Type |  |  |  |  |  |  |  |  |  |  |
| 1 05:49 -60 -787 Sunrise 2 06:49 0 -727 Sunrise 3 18:56 727 0 Sunset 4 22:00 911 184 Sunset |  |  |  |  |  |  |  |  |  |  |
|  |  | NEXT |  | T / R / S |  | O K |  |  |  | QUIT |

- Time (hh:mm):	specifies the clock time for the start of the period.

- Sunrise (min): specifies the start time relative to sunrise.

- Sunset (min): specifies the start time relative to sunset.

- Type: specifies whether the period start time is fixed to a clock time or is relative to sunrise or sunset.

COMMENT

In certain programming menus the   PERIOD    key appears in the option line indicating that different settings are possible for each period.

### Start time attachment

Press the   T/ R / S    key to specify whether the period start time is absolute (clock Time), or relative (tied to sunRise or sunSet).

## Transition Times

COMPART  OTHER   PERIODS  NEXT

- Transition time determines the set-point gradient between consecutive periods.

# WEATHER MONITORING STATION

- Rain, frost, wind and storm thresholds.

- Configurable wind speed and solar radiation readings.

- Wind vane influence (wind speed).

## Settings

GENERAL  WEATHER

| 1. Rain detection: a threshold of ‘100%’ disables the sensor, a threshold of ‘0%’ results in permanent detection. Gen. weather station settings |  |  |  |  |  |  |  |  |  | 10 : 12 : 15 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Rain detection threshold [ 0 – 100 % ] Delay before deactivate rain [ 0 – 240 min ] Frost detection threshold [ -25/+40 °C ] Storm wind speed threshold [ 0 – 72 km/h ] Delay before deactivate storm [ 0 – 240 min ] Sync. vents if storm detected [ Yes / No ] Fix vent pos storm detected [ Yes / No ] N° of o/p activate storm conditions [ 0 – 256 ] Threshold for maximum wind speed [ 0 – 150 Km/h ] Wind speed tolerance [ 0 – 150 Km/h ] Time maintain max wind speed [ 0 – 500 min ] Calc. wind speed average over [ 0 – 20 min ] Calc. sol. radiation average over [ -10 /+10 min ] |  |  |  |  |  |  | : : : : : : : : : : : : : | 50 2 - 2.0 70 10 YES YES 0 15 5 5 1 3 |  |  |  | % min °C Km/h min Km/h Km/h min min min |
| OTHER |  | RAIN |  |  |  | MODIFY |  |  |  |  | QUIT |  |

1

2

3

4

Fix a delay before rain status clears after rain has stopped.

Set the outside temperature threshold for frost detection.

- 2. Storm detection: wind speed threshold.

Fix a delay before storm status clears after the wind speed has dropped. Specify if vents should synchronize (to 0%).

Specify if the vent should obey the maximum position safety setting (see Vents). Specify the number of the output to be activated.

### Configuring the wind speed reading

    - 3. Set a ‘Threshold for maximum wind speed’ (<< storm). The readings are calculated as follows.

Below the threshold

The reading, which is updated every minute, shows the average anemometer measurement over the period set by the ‘Calculate wind speed over’ parameter.

Above the threshold

As anemometer measurements  increase the reading shows the peak value over the previous minute. As wind speed decreases the reading keeps the last peak anemometer measurement for a period defined by ‘Time maintain maximum wind speed’.

To limit fluctuations, the reading is updated only if the new measurement exceeds the ‘Wind speed tolerance’ setting.

### Configuring the solar radiation reading

    - 4. This setting defines the update interval for the average reading.

Entry X < 0: reading is updated every minute but equals the average over the last X minutes.

Entry X > 0: reading is updated every X minutes but equals the average over the last minute.

## Wind Influences

GENERAL    WEATHER    OTHER

| 1. Update interval of the wind vane reading. Influences on wind direction |  |  |  |  |  |  |  |  |  | 10 : 12 : 15 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Wind dir. change timeout [ 0 – 500 min ] Wind speed for min influence [ 0 – 72 km/h ] Wind speed for max influence [ 0 – 72 km/h ] Max infl. on w. dir. timeout [ 0 – 500 min ] |  |  |  |  |  |  | : : : : | 60 18 36 90 |  |  |  | min Km/h Km/h % |
|  |  |  |  |  |  | MODIFY |  |  |  |  | QUIT |  |

1

2

- 2. Wind speed thresholds define a range of influence on the duration of the timeout interval.

Maximum reduction of the interval at maximum wind speed influence.

## Rain gauge (option only)

GENERAL    WEATHER   RAIN

| The sensor settings include: the number of cubic millimeters corresponding to one output pulse; the rainfall collection surface area (cm²) of the sensor. Gen weather station settings |  |  |  |  |  |  |  |  |  | 10 : 12 : 15 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Volume of water per pulse [ 0 – 10000 mm ] Sensor surface area [ 0 – 10000 cm² ] |  |  |  |  |  |  | : : | 5 50 |  |  |  | mm3 cm² |
|  |  |  |  |  |  | MODIFY |  |  |  |  | QUIT |  |

# VENTS

- Proportional control plus settings for stabilization.

- Influences: outside temperature, wind, solar radiation (but also see other chapters).

- Safety settings for storm, rain and frost.

The set-point position is proportional to the difference between the ventilation temperature set-point and the ambient temperature measurement. Control can be influenced by weather, safety positions, humidity and operations such as fumigation.

## Setting up control

COMPART    VENT

| 1. ‘Ventilation temperature’ is the compartment set-point temperature for control of leeward vents. Vent settings comp 1 |  |  |  |  |  |  |  |  |  | 10 : 12 : 15 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Roof leeward side, 05:53L/18:00C (2) |  |  |  |  |  |  |  |  |  |  |  |  |
| Ventilation temperature [ -10/+ 40 °C ] Ventilation temperature offset [ 0 – 40 °C ] Maximum vent position [ 0 – 100 % ] Minimum vent position [ 0 – 100 % ] |  |  |  |  |  |  | : : : : : | 18.0 2 80 10 |  |  |  | °C °C % % |
| PERIOD |  | VNT TYP |  | OTHER |  | MODIFY |  |  |  |  | QUIT |  |

1

2

The ‘Ventilation temperature offset’ fixes the set-point for windward vents relative to the ventilation temperature and is a differential not an absolute temperature!

- 2. Specify the maximum and minimum (‘crack’) opening limits.

## Influences

### Outside temperature

COMPART    VENTS    OTHER     INFLUE   OST INF

| 1. Enter temperature thresholds for the influence range. Influences on vents comp 1 |  |  |  |  |  |  |  |  |  | 10 : 12 : 15 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Roof leeward side |  |  |  |  |  |  |  |  |  |  |  |  |
| Outside T for start of influ. [ -25/+40 °C] Outside T for max influence [ -25/+40 °C] Max influ. on p-band temp [ 0 – 5 °C ] Max influ. on max vent pos [ 0 – 100% ] Min percentage corr. max pos [ 0 – 100% ] Influ. on min vent position [ Yes / No ] |  |  |  |  |  |  | : : : : : : | 8.0 1.0 3.0 20 10 YES |  |  |  | °C °C °C % % |
|  |  | VNT TYP |  |  |  | MODIFY |  |  |  |  | QUIT |  |

1

2

3

4

- 2. The ‘Maximum influ. on P-band temp’ specifies the maximum permitted change to the temperature setting for proportional control (see §7.4 for an explanation of P-band).

- 3. Specify the maximum change (+ve or -ve) applied to the maximum position.

Specify the minimum permitted correction to the maximum position as the influence decreases (excludes minor changes).

- 4. If entry = Yes, the influence is also applied to the minimum vent position.

### Wind speed

COMPART    VENTS    OTHER     INFLUE    WSP INF

| 1, 2 & 3. See the outside temperature influence for an explanation of the settings. Influences on vents comp 1 |  |  |  |  |  |  |  |  |  | 10 : 12 : 15 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Roof leeward side |  |  |  |  |  |  |  |  |  |  |  |  |
| Min wind speed influence [ 0 – 72 km/h ] Max wind speed influence [ 0 – 72 km/h ] Max influ. on p-band temp [ 0 – 50 °C ] Max influ. on max vent pos [ 0 – 100% ] Min percentage corr. max pos [ 0 – 100% ] Influ. on min open position [ Yes / No ] |  |  |  |  |  |  | : : : : : | 15 35 5.0 40 10 YES |  |  |  | Km/h Km/h °C % % |
|  |  | VNT TYP |  |  |  | MODIFY |  |  |  |  | QUIT |  |

1

2

3

4

### Solar radiation

COMPART    VENTS    OTHER     INFLUE    RAD INF

| 1. Enter thresholds to define the influence range. Influences on vents comp 1 |  |  |  |  |  |  |  |  |  | 10 : 12 : 15 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Rad. for minimum influence [ 0 – 1000 W/m² ] Rad. for maximum influence [ 0 – 1000 W/m² ] Max infl. on ventilation temp [ -40 /+40 °C ] Max influ. on max vent position [ -100 /+100 % ] Min percentage correction pos max [ 0 – 100 % ] Overshoot max open pos [ Yes / No ] Start time [ 00:00 - 23:59 ] End time [ 00:00 - 23:59 ] |  |  |  |  |  |  | : : : : : : : : | 200 400 - 2.0 10 10 NO 120 -120 |  |  |  | W/m² W/m² °C % % SR SS |
|  |  |  |  |  |  | MODIFY |  |  |  |  | QUIT |  |

1

2

3

4

5

- 2. Maximum change (+ve or -ve) applied to the ventilation set-point temperature.

- 3. Maximum change (+ve or -ve) applied to the maximum position. Minimum amount of correction to maximum position (excludes minor changes).

- 4. Allows the solar radiation influence to extend vent opening beyond the maximum position.  CAUTION: this influence now determines the maximum opening of the vent.

- 5. Period over which the influence is active.

Example of external influences

|  | Leeward vent | Windward vent |
| --- | --- | --- |
| Max position | 60 % | 50 % |
| Max wind speed influence | 30 % | 30 % |
| Max outside temperature influence | 20 % | 20 % |
| Max sunlight intensity influence | +10 % | +10 % |
| Max vent position with wind and temperature influences at maximum | 60 - 30 -20 = 10% | 50 - 30 - 20 = 0% |
| Max vent position with wind and temperature influences at maximum PLUS max sunlight intensity influence (e.g. strong sunlight) | 60 - 30 -20 +10 = 20% | 50 - 30 - 20 +10 = 10% |

## Safety Settings

COMPART    VENT    OTHER     SAFETY

| 1. Enter the rain, frost and storm maximum vent positions. Vent safety position comp 1 |  |  |  |  |  |  |  |  |  | 10 : 12 : 15 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Roof leeward side |  |  |  |  |  |  |  |  |  |  |  |  |
| Max position rain detected [ 0 – 100 % ] Max position frost detected [ 0 – 100 % ] Max position storm detected [ 0 – 100 % ] Vent alarm delay [ 0 – 120 min ] Percentage error for alarm [ 0 – 100 % ] O/s humidity close vents, drying [ 0 – 100 % ] |  |  |  |  |  |  | : : : : : | 10 2 1 0 5 0 |  |  |  | % % % min % % |
|  |  | VNT TYP |  |  |  | MODIFY |  |  |  |  | QUIT |  |

1

2

3

- 2. ‘Percentage error for alarm’ threshold is the difference between the vent position and set-point that generates an alarm condition. The alarm activates if the error is still present when the delay times out.

Note: the settings apply only if a position sensor exists (see §7.5).

- 3. Outside humidity above this threshold suspends opening for dehumidification.

## General Configuration

COMPART    VENT    OTHER     GENERAL

| 1. This setting defines a narrow temperature band (+/-) for control determined by the ‘Cumulative (or integral) percentage correction’ (see 5 below). General vent settings comp 1 |  |  |  |  |  |  |  |  |  | 10 : 12 : 15 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Control temp difference [ 0 – 40°C ] Vent control interval [ 0 – 120min ] Min percentage correction [ 0 – 50% ] Min percentage corr. at 100% [ 0 – 50% ] Max percentage correction [ 0 – 100% ] Vent p-band T at 100% (lee) [ 0 – 50°C ] Vent p-band T at 100% (wind) [ 0 – 50°C ] Cumulative percent. correction [ 0 – 100% ] Trend percentage correction [ 0 – 100% ] P-band based on max pos [ Yes / No ] |  |  |  |  |  |  | : : : : : : : : : : | 0.5 1 3 10 50 10.0 10.0 2 2 NO |  |  |  | °C min % % % °C °C % % |
|  |  |  |  |  |  | MODIFY |  |  |  |  | QUIT |  |

1

2

3

4

5

6

7

Note: a wide band (e.g. > 1°C) can lead to poor stabilization.

- 2. Specify the duration of the control cycle.

- 3. Specify a minimum amount of correction over 1 control cycle, and the minimum amount of correction at the fully open position (to limit oscillation). This means that minimum control is calculated proportionally over the range defined by these two settings ( i.e. in the menu, the min. correction = 10% at 100%, 5% at 50%, and 3% at 30% open and below).

The ‘Max percentage correction’ specifies the maximum amount of correction over I control cycle.

P-band at 100%

- 4. The P-band temperature specifies the number of degrees of ambient temperature above the ventilation temperature set-point at which the vent is fully open (i.e.100%). Control is proportional over this temperature range.

Note: a narrow band produces faster movement, and vice versa.

- 5. Specify the amount of correction for narrow band ambient–to-ventilation temperature differences (see 1 above).

Note: the correction is added or subtracted for increasing or decreasing temperature differences, respectively. However, it  takes effect only if its totalized value is greater than the minimum correction (see 3. above). The total is automatically zeroed when the vents are synchronized or if the ambient temperature < ventilation temperature set-point.

- 6. The ‘Trend percentage correction’ contributes to a correction based on the rate of change of ambient temperature over 1 control cycle.

Note: % change = (∆t° per control cycle) x (trend correction) / (control temperature differential).

- 7. If  ‘P-band based on max pos’ = YES, proportional control is based on the ‘Maximum vent position’ instead of 100% open.

## Physical Configuration

COMPART    VENT    OTHER    SAFETY   CFG. VEN

| 1. Specify the total measured time open / close times between 0% and 100%. Configuration vent compartment 1 |  |  |  |  |  |  |  |  |  | 10 : 12 : 15 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Vent 1 / Vent 2 |  |  |  |  |  |  |  |  |  |  |  |  |
| Overall time to open [ 0 – 1200 sec ] Overall time to close [ 0 – 1200 sec ] Number of vent to follow [ 0 – N vents ] Time after end travel [ 0 – 300 sec ] Temperature sensor [ T1 / T2 / T1,T2] Vent position sensor [ Yes / No ] Sensor error correction [ 50 - 1000 ] |  |  |  |  |  |  | : : : : : : : | 78 77 0 0 T1 NO 50 |  |  |  | sec sec sec |
|  |  | TYP VNT |  |  |  | MODIFY |  |  |  |  | QUIT |  |

1

2

3

4

5

- 2. If the  entry = 0, the  compartment settings apply, otherwise the vent obeys the settings of the numbered vent.

- 3. Specify a ‘backlash’ time to ensure full take-up for all vents on a common shaft at the ‘0%’ and ‘100%’ positions.

- 4. If there are two shelters, select which one is to provide the T° measurement: T1, T2 or T1/T2 for the average of both.

Position sensor and error correction

- 5. Enable the sensor if present. Specify an error correction threshold, which is expressed in units of 1/100ths of a second (50  0.5 sec, 1000  10 sec) and should correspond to a percentage of the overall open–close time of the vent.

If the position given by the sensor differs from the set-point by an amount that exceeds the equivalent of the error correction, the vent is forced to the set-point position.

Note: these settings are normally determined by the installer during commissioning and should not require alteration.

## Compartment Orientation

COMPART    VENT    OTHER    SAFETY   VNT CFG

| This is the bearing of the main axis of the compartment taken in a clockwise direction with respect to North, with vent n°1 on the left. Together with the wind vane readings it determines leeward or windward control of the vent. Note: with the wind vane reading correctly, check that the leeward vent opens more than the windward vent. If not, the figure for orientation may be 180° in error. Configuration vent compartment 1 |  |  |  |  |  |  |  |  |  | 10 : 12 : 15 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Compartment orientation [ 0 – 360° C] |  |  |  |  |  |  | : | 30 |  |  |  | deg |
|  |  |  |  |  |  | MODIFY |  |  |  |  | QUIT |  |

## Synchronization

COMPART    VENT    OTHER   SYNCHRO

| Definition Set-points general |  |  |  |  |  |  |  |  |  | 10 : 12 : 15 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Synchronization time [ 00:00 – 23:59 ] Synchronization time [ 00:00 – 23:59 ] Max position start synchronization [ 0 – 100% ] Synchronization interval [ 0 – 1440 min ] Synchronization at 0 % [ Yes /No ] |  |  |  |  |  |  | : : : : : | 08:00 17:00 20 120 NO |  |  |  | % min |
|  |  |  |  |  |  | MODIFY |  |  |  |  | QUIT |  |

The vent is forced fully open or closed depending on the current set-point (greater or less than ‘50%’, respectively): normal control then continues.

- Synchronization can occur at two clock times. Enter ‘00:00’ to cancel a time.

- ‘Max pos. start synchronization’ defines an offset above minimum opening. If its set-point is within this range the vent is synchronized after each ‘Synchronization interval’.

- If ‘Synchronize at 0%’ = Yes, the vent always closes when synchronized.

# HumidIty control

- Standard control mode covers a 24hr period.

- Different control modes possible for each of the four Climat Periods.

- Vent and heating influences.

## Introduction

Relative Humidity (RH) is a ratio expressing the amount of moisture in the surrounding air compared to the amount when air is saturated.

Saturation Deficit (mBar) is an expression of the quantity of moisture the surrounding air can absorb at a given temperature before reaching saturation.

For any given temperature low humidity corresponds to high saturation deficit, and vice versa.

The graphs show the relationship between Saturation Deficit, Relative Humidity and Temperature, and include an example showing an ‘ideal zone’ of working defined by the following characteristics:

minimum and maximum saturation deficit	= 3mBar and 6 mbar

minimum and maximum temperatures		= 16 °C and 19°C.

In this example (for PERIOD 1 in the menu shown overleaf) humidity should ideally remain between 67% and 86%. Outside these limits humidity control influences on the vents, heating or both will act to bring the environmental conditions of the compartment back within the working zone within the minimum and maximum temperature limits.

## Set-point Monitoring

COMPART    HUMIDTY

| For each Climat period there are two pairs of temperature/humidity figures corresponding to the low and high saturation deficit setpoints shown on the left (3mBar and 6mBar). Sat. def. (Temp/humid) comp 1 |  |  |  |  |  |  |  |  | 10 : 12 : 15 |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 06:22R 07:22R 20:31S 23:31S |  |  |  |  |  |  |  |  |  |  |
| Def Per 1 Per 2 Per 3 Per 4 |  |  |  |  |  |  |  |  |  |  |
| 3.0 19.0 86 18.0 85 19.0 86 20.0 87 6.0 16.0 67 15.0 64 16.0 67 17.0 69 |  |  |  |  |  |  |  |  |  |  |
| VNT CTL |  | HTG CTL |  | FOG |  | MODIFY |  |  |  | QUIT |

Note: see the explanation and graphs on the previous page.

[Def  = Saturation deficit; Per  = Period ]

## Setting Up Control

COMPART    HUMIDTY    MODIFY

| Saturation deficit compartment 1 |  |  |  |  |  |  |  |  |  | 10 : 12 : 15 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Lower sat. deficit limit [ 0 - 50 mBar ] Upper sat. deficit limit [ 0 - 50 mBar ] Maximum permitted temperature [ 0 - 50 °C ] Minimum permitted temperature [ 0 - 50 °C ] Vent control delay [ 0 – 1440 min ] Drying cycle interval [ 0 – 1440 min ] Max T° diff. min RH infl. on vents [ 0 – 40 °C ] Stop heating for T°/RH max [ Yes / No ] Humidity control mode [ 1, 2, or 3 ] Min humidity influence on Max Pos [ Yes / No ] Lee / Wind sequence [ Yes / No ] |  |  |  |  |  |  | : : : : : | 3.0 6.0 28.0 5.0 5 30 0.5 NO 1 NO NO |  |  |  | mBar mBar °C °C min min °C |
|  |  |  |  |  |  | O K |  |  |  |  | QUIT |  |

1

2

3

4

5

6

7

- 1. Enter saturation deficit set-points for the control of humidity, and min/max temperatures to define the effective limits.

Note: humidity control is suspended outside this temperature range.

Starting dehumidification

- 2. When heating is turned ON a delay occurs before the opening of the vent.

The ‘Drying cycle interval’ is the time between successive periods of dehumidification.

- (3) This setting defines the number of degrees below maximum temperature at which control to compensate for low humidity begins to influence the vent. This allows fine control of the vent at temperatures close to maximum, thus reducing any open/close conflicts that might otherwise occur.

- (4) Enter Yes to turn heating OFF if temperature and humidity exceed their maximum permitted levels.

Choosing a control mode

- (5) The possibilities are as follows:

Entry = 1:	 24 hour control is based on the Saturation Deficit set-points specified in this menu.

Entry = 2: 	control is programmable per Period and based on Relative Humidity (set-points entered in the influence menu).

Entry = 3	control is programmable per Period and based on Saturation Deficit (set-points entered in the influence menu).

- 6. If entry = Yes, low humidity influences the vent maximum position otherwise, if entry = No, it influences the vent set-point.

7. If entry = Yes, control in response to high humidity alternates between the leeward and windward vents (despite the fact that programming for humidity is common to both).

## Influences On Vent Control

COMPART   HUMIDTY    VNT CTL

| Excess humidity Humid influ. on heating comp 1 |  |  |  |  |  |  |  |  |  | 10 : 12 : 15 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Roof lee side, 05:53R/18:00S (2) |  |  |  |  |  |  |  |  |  |  |  |  |
| Hum influence on vent position [ 0 – 10 %/% ] Max vent pos for RH influ [ 0 – 100 % ] Reduction max pos, o/s T° influ. [ 0 – 100 % ] Reduction max pos, wind influ. [ 0 – 100 % ] Min humid. influ. on vent position [ 0 – 10 %/% ] Diff max vent pos min humid. Influ. [ 0 – 100 % ] Maximum humidity [ 0 - 100% ] Minimum humidity [ 0 - 100% ] Minimum deficit [ 0 - 50 mBar ] Maximum deficit [ 0 - 50 mBar ] |  |  |  |  |  |  | : : : : : : : : : : | 1.5 20 10 5 0.5 20 60 85 2.0 7.0 |  |  |  | %/% % % % %/% % % % mBar mBar |
| PERIOD |  | VNT TYP |  |  |  | MODIFY |  |  |  |  | QUIT |  |

1

2

3

- 1. Percentage increase in vent opening per percentage of excess humidity.

Maximum opening under high humidity control.

Reduction of maximum opening due to outside temperature and wind speed influences (using the ranges already specified for vent influences – see §Vents).

Low humidity

- 2. Percentage decrease in vent opening per percentage of humidity lacking.

‘Diff max vent pos min humid. influ’ limits the difference between the low and high humidity positions.

REMINDER: these influences are only valid if the compartment temperature is below the ‘Maximum permitted temperature’.

Control mode

- 3. These settings relate directly to control modes 2 and 3 in the previous menu (and not to influences).

## Influences On Heating

COMPART    HUMID    HTG CTL

| Dehumidification Humid influ. on heating comp 1 |  |  |  |  |  |  |  |  |  | 10 : 12 : 15 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Roof lee side, 05:53R/18:00S (2) |  |  |  |  |  |  |  |  |  |  |  |  |
| Influ. on water temperature [ 0 – 130 °C/% ] Max infl on calculated water T [ 0 – 130 °C ] Influence Hmin. on water temp. [ +/- 130 °C/% ] Max influ on calculated water T [ 0 – 130 °C ] Influence Hmin. on min water temp. [+/- 130 °C/%] Max influ on minimum water T [ 0 – 130 °C ] |  |  |  |  |  |  | : : : : : : | 3.0 20.0 2.0 15.0 5.0 20.0 |  |  |  | °C / % °C °C / % °C °C /% °C |
| PERIOD |  | TYP HTG |  |  |  | MODIFY |  |  |  |  | QUIT |  |

1

2

- 1. Number of °C increase in the heating water set-point per percentage excess humidity.

Maximum set-point increase.

Note: use in combination with the vent influence to remove excess humidity.

Low humidity

- 2. Number of °C change (+ve or –ve) in the heating set-point and minimum water temperatures per percentage humidity lacking.

Maximum changes to set-points.

Note: increase or decrease these set-points according to the desired strategy.

# HOT WATER HEATING

- Compartment set-points and water temperature thresholds per heating loop and per PERIOD.

- Influences: outside temperature, wind speed and solar radiation.

- Configuration of heating loop regulation.

- Safety parameters.

Mixing valve

set-point

(calc.)

Pump ON (2)

(ambient T°)

(calc.)

Ambient T°

set-point

(calc.)

)

Kp, Ki, Kd

Max water T° var. per interval

Ambient T°

(meas)

Pump ON (1)

(water T°)

(calc.)

Water T°

(meas.)

Diff.

Diff.

Diff.

Water T°

set-point

(calc.)

## Setting Up Control

COMPART    HEATING

| A compartment heating loop requests heat when the temperature measurement falls below the set-point. Heating set-points compartment 1 |  |  |  |  |  |  |  |  |  | 10 : 12 : 15 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| High temperature heating, 05:53L/18:00C (2) |  |  |  |  |  |  |  |  |  |  |  |  |
| Ambient temperature [ -10/+40 °C ] Ground temperature [ -10/+40 °C ] Minimum water temperature [ 0 – 90 °C ] Maximum water temperature [ 0 – 130 °C ] |  |  |  |  |  |  | : : : : : | 16.0 15.0 30.0 70.0 |  |  |  | °C °C °C °C |
| PERIOD |  | TYP HTG |  | OTHER |  | MODIFY |  |  |  |  | QUIT |  |

- The Ambient and Ground (=substrate) temperatures are the set-points controlling the pipe water temperature in the respective heating loops.

‘Maximum /minimum water temperature’ define upper and lower pipe temperature thresholds for the heating loops: main (tube-rail), secondary (grow) and ground heating.

IMPORTANT

The reference for ambient temperature is the T°/RH sensor shelter (or measuring box) in the compartment. Shelters must be sited away from direct sunlight, air currents, and any obstacles likely to prevent the free flow of air through them. Ground temperature measurements are usually obtained from a sensor placed in the substrate.

- PERIOD     :	= next period.

- TYP HTG    :	= next heating loop.

## Influences

### Outside temperature

As the outside temperature falls the minimum water temperature set-point is increased.

COMPART    HEATING   OTHER     INFLUE.   OST INF

| The two outside temperature settings define the influence range. Influence on heating, compartment 1 |  |  |  |  |  |  |  |  |  | 10 : 12 : 15 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| High temperature heating, 05:53L/18:00C (2) |  |  |  |  |  |  |  |  |  |  |  |  |
| Outside T° for min influence [ -25/+20 °C ] Outside T° for max influence [ -25/+20 °C ] Max infl. on min water temp [ 0 – 50 °C ] |  |  |  |  |  |  | : : : | 8.0 -5.0 10.0 |  |  |  | °C °C °C |
|  |  | TYP HTG |  |  |  | MODIFY |  |  |  |  | QUIT |  |

‘Max. influ. on min. water temp.’ defines the number of degrees increase in the minimum water temperature at maximum influence. The effect is proportional over the range.

### Wind speed

As wind speed increases the minimum water temperature set-point is increased.

COMPART    HEATING    OTHER     INFLUE    WSP INF

| The two wind speed settings define the influence range. Influence on heating, compartment 1 |  |  |  |  |  |  |  |  |  | 10 : 12 : 15 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| High temperature heating, 05:53L/18:00C (2) |  |  |  |  |  |  |  |  |  |  |  |  |
| Wind speed for min influence [ 0 – 72 km/h ] Wind speed for max influence [ 0 – 72 km/h ] Max infl. on min water temp [ 0 – 50 °C ] |  |  |  |  |  |  | : : : | 15 35 5.0 |  |  |  | km/h km/h °C |
|  |  | TYP HTG |  |  |  | MODIFY |  |  |  |  | QUIT |  |

‘Max. influ. on min. water temp.’ defines the amount of increase in the minimum water temperature at maximum influence. The effect is proportional over the range.

### Solar radiation

As direct solar radiation increases the minimum water and ambient temperature set-points are reduced.

As accumulated solar radiation is totalized the ambient and ventilation temperature set-points are reduced and increased, respectively.

COMPART    HEATING    OTHER     INFLUE    RAD INF

| 1. Program start and end times for the influence. Influence on heating, compartment 1 |  |  |  |  |  |  |  |  |  | 10 : 12 : 15 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| High temperature heating, 05:53L/18:00C (2) |  |  |  |  |  |  |  |  |  |  |  |  |
| Time start influence active [ 00:00 - 23:59 ] Time end influence active [ 00:00 - 23:59 ] Radiation for min influence [ 0 – 1000 W/m² ] Radiation for max influence [ 0 – 1000 W/m² ] Max influence on ambient temp. [ -40/+40 °C ] Max influence on min water temp. [ -100/+100 °C ] Accum. radiation for min influence [0 – 1000 Wh/m² ] Accum. radiation for max influence [0 – 1000 Wh/m² ] Max influence on ambient temp. [ -40/+40 °C ] Max influence on ventilation temp. [ -40/+40 °C ] Time start influence active [ 00:00 - 23:59 ] Time end influence active [ 00:00 - 23:59 ] |  |  |  |  |  |  | : : : : : : : : : : : : | 400 600 -3.0 -10.0 1000 2000 -4.5 2.0 30 23:00 |  |  |  | SR FT W/m² W/m² °C °C Wh/m² Wh/m² °C °C SS HF |
|  |  | TYP HTG |  |  |  | MODIFY |  |  |  |  | QUIT |  |

1

2

Two settings for direct solar radiation define the influence range.

‘Max. influ. on min. water temp.’ and ‘Max. influ. on ambient temp.’ set the the amount of increase or decrease (-ve entry)  in the minimum pipe and ambient temperatures at maximum influence. The effect is proportional over the range.

- 2. Two settings for accumulated solar radiation define the influence range.

‘Max. influ. on ambient temp.’ and ‘Max. influ. on ventilation temp.’ set the amount of increase and decrease (-ve entry), respectively, at maximum influence. The effect is proportional over the range.

Program start and end times for the influence.

Note: the accumulated radiation totalizer is reset to ‘0’ at the start of period 1 of compartment 1.

## Configuration

COMPART    HEATING   OTHER     HTG CFG

| Heating loop regulation. Configuration heating comp 1 |  |  |  |  |  |  |  |  |  | 10 : 12 : 15 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Heating 1 |  |  |  |  |  |  |  |  |  |  |  |  |
| Heating control interval [ 0 – 30 min ] Ki, control point coefficient [ 0 - 10 ] Kd, heating trend coefficient [ 0 - 100 ] Kp, water temp coefficient [ 0 - 10 ] Max water T var. per interval [ 0 - 10 °C] Water T diff. to control 3WV [ 0 - 10 °C ] Min 3WV control time per °C [ 0 – 120 sec ] Max 3WV control time per °C [ 0 – 120 sec ] Water T° diff. infl min ctrl time [ 0 – 130 °C ] Water T° diff. infl max ctrl time [ 0 – 130 °C ] 3WV overall control time [ 0 – 120 sec ] Open 3WV (at boiler 3WV temp) [ Yes / No ] Heating pump ON, water temp [ 0 – 130 °C ] Heating pump ON, ambient temp [ 0 – 130 °C ] 3WV and pump service interval [ 0 – 500 hr ] Flow rate for energy calc. [ 0 - 1000 m3/h] Stop pump at blr T closes 3WV [ Yes / No ] Delay before pump stops [ 0 – 1440 min ] Temperature sensor [T1,T2,T1/T2, Ts ] Number of compartment to follow [ ] |  |  |  |  |  |  | : : : : : : : : : : : : : : : : : : : : | 1 0.8 0.0 3.0 5.0 2.0 2.0 7.0 50 10 210 NO 12.0 1.0 120 5.5 YES 1 T1 |  |  |  | min °C °C sec/°C sec/°C °C °C sec °C °C hr m3/h min |
|  |  | TYP HTG |  |  |  | MODIFY |  |  |  |  | QUIT |  |

1

2

3

4

- 1. Set the control interval (cycle).

‘Ki control point coefficient’ reduces under/overshoot in the regulation process.

‘Kd control point coefficient’ reduces the trend towards large set-point variations over successive control cycles. For initial set up a value of Kd slightly less than Kp is recommended.

‘Kp control point coefficient’ is the proportional factor in the pipe temperature set-point calculation. For every 1°C temperature change required in the compartment the pipe set-point temperature is increased by Kp degrees.

The variation in pipe temperature per control cycle is limited to a maximum.

Mixing valve regulation

- 2. ‘Water T° diff. to control 3WV’ specifies the minimum pipe temperature difference (measurement – set-point) required to start regulation.

The ‘Minimum / maximum control time per °C’ settings specify control rates corresponding to high and low temperature differences, which are defined by the ‘Water T° diff. infl min /max ctrl time’ settings.

The regulation of the valve is a function of the control rate for any given temperature difference and of its ‘Overall control time’, which is the total response time from 0% to 100% open.

If ‘Open 3WV at blr T° opens 3WV’ = Yes, the mixing valve is forced to open when the boiler reaches the safety threshold at which it opens all heating loop valves (see boiler settings).

Recirculating (heating) Pump start conditions

- 3. ‘Heating pump ON, water temp’ specifies a floating offset from the pipe set-point temperature. When the ambient temperature measurement is beyond the offset the pump is ON.

‘Heating pump ON, ambient temp’ specifies a floating offset from the ambient temperature set-point. When the ambient temperature measurement is within the offset the pump is ON.

Note: the pump turns ON if either condition is valid.

Miscellaneous settings

- 4) ‘3WV and pump service interval’ is the duration of pump inactivity that causes both pump and mixing valve to operate for 1 minute (to maintain serviceability).

‘Flow rate for energy calc’ specifies a theoretical flow rate in the heating loops (return water temperature sensor required).

‘Stop pump at blr T closes 3WV’ = Yes causes pump to stop when the boiler reaches the safety threshold opening all heating loop mixing valves (see boiler config.).

‘Delay before pump stops’ introduces an interval between the OFF command and the pump stopping.

Use ‘Temperature sensor’ to select the sensor shelter providing the temperature measurement, that is T1, T2 or T1/T2 for the average of both if there are two shelters.

Note: a ground heating loop includes the Ts (ground temperature sensor) option.

‘Number of compartment to follow’: enter ‘0’ for the current compartment or the number of another compartment as the source of the temperature measurement.

## Safety settings

COMPART    HEATING    OTHER     SAFETY

| 1. The minimum water temperature is overridden (forced to 0°C) if the ambient temperature exceeds the set-point by the amount of this offset. Configuration heating comp 1 |  |  |  |  |  |  |  |  |  | 10 : 12 : 15 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| High temperature heating |  |  |  |  |  |  |  |  |  |  |  |  |
| Amb. T° diff. cancels min wtr T [ 0 – 50 °C ] Water T diff. triggers alarm [ 0 – 130 °C ] Alarm delay [ 0 – 1440 min ] |  |  |  |  |  |  | : : : | 2.0 10.0 60 |  |  |  | °C °C min |
| PERIOD |  | TYP HTG |  |  |  | MODIFY |  |  |  |  | QUIT |  |

1

2

- 2. If the pipe temperature exceeds the set-point by the amount of this offset an alarm activates once the alarm delay has timed out (and the temperature excess remains).

Note: the mixing valve is opened.

# BOILER CONTROL

- Min / max temperature alarms and safety settings.

- Normal, high-firing and modulated burner control.

- Special period working (e.g. reduced output, standby).

## Setting Up Control

GENERAL    HEATING   BOILER

| Note: the settings have been regrouped in the menu to improve clarity. Settings boiler 1 |  |  |  |  |  |  |  |  |  | 10 : 12 : 15 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Boiler on line [ Yes / No ] Min water temp limit for alarm [ 0 – 130 °C ] Max water temp limit for alarm [ 0 – 130 °C ] Delay before alarm activates [ 0 – 1440 min ] Water temp closes valves [ 0 – 130 °C ] Water temp opens valves [ 0 – 130 °C ] Minimum water temperature [ 0 – 130 °C ] Maximum water temperature [ 0 – 130 °C ] Water T diff. stops burner [ 1 – 130 °C ] Boiler water temp increase [ 0 – 100 % ] Min return water temp. alarm [ 0 – 130 °C ] Max return water temp. alarm [ 0 – 130 °C ] |  |  |  |  |  |  | : : : : : : : : : : : : | YES 55 95 10 60 95 80 90 4.0 5 55.0 98.0 |  |  |  | °C °C min °C °C °C °C °C % °C °C |
| BLR N° |  | STORAGE |  | OTHER |  | MODIFY |  |  |  |  | QUIT |  |

1

2

3

4

- 1. Set min and max alarm thresholds on the boiler water temperature.

Specify an alarm delay time.

Protection

- 2. ‘Water temperature closes valves’ specifies the low temperature threshold below which all heating loop mixing valves close in order to reduce the possibility of boiler condensation / corrosion.

‘Water temperature opens valves’ specifies the high temperature threshold above which all heating loop mixing valves open in order to dissipate surplus boiler heat.

Note: these settings are inactive if: the boiler is not on line, or the boiler is on standby, or an outside temperature influence has deactivated the boiler , or the outside temperature > boiler follow-on working temperature 2.

Boiler temperature operating range

- 3. The minimum and maximum water temperatures define the operating range.

The ‘Water T° diff stops burner’ defines an offset from the boiler set-point temperature: the burner shuts OFF if the temperature difference is exceeded.

‘Boiler water temp increase’ determines the boiler set-point temperature, which equals the highest supplied transport or heating loop set-point temperature increased by this percentage.

Return temperature alarms

- 4. Specify the minimum and maximum return water temperature alarm thresholds.

Note: in order to increase the boiler return temperature in response to a low temperature alarm, the compartment mixing valves close progressively over a six minute period.

Note: in the case of a boiler mixing valve (or variable speed pump) you are advised to enter a very low minimum alarm threshold.

IMPORTANT

These alarms are inoperative unless the boiler is activated and the alarm delay > 1 minute.

## Configuration

GENERAL    HEATING   BOILER   OTHER   CFG BLR

| Burner regulation Settings configuration boiler 1 |  |  |  |  |  |  |  |  |  | 10 : 12 : 15 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Burner control interval [ 0 – 60 sec * 5 ] Kp boiler coeff. (sec/ 1deg) [1 – 10 sec/1deg ] Kd boiler coeff. (sec/ 1deg) [1 – 10 sec/1deg ] Difference starts burner [ -50/+50 °C ] Initial burner control delay [ 0 – 600 sec ] Overall burner control time [ 0 – 1200 sec ] Minimum boiler ON time [ 0 – 600 sec ] Max burner pos, aux period [ 0 – 100 % ] Burner position deviation [ ] Burner alarm delay [ ] Burner position input n° [ ] Recirculating pump output n° [ ] Recirculating pump ON time [ ] ON/OFF output n° (stop modul) [ ] |  |  |  |  |  |  | : : : : | 12 1.0 0.5 0..2 90 40 120 30 |  |  |  | x 5 s °C sec sec sec % % % sec sec |
| BLR N° |  |  |  |  |  | MODIFY |  |  |  |  | QUIT |  |

1

2

3

4

- 1. Specify the interval between burner control events (=control cycle).

Kp and Kd are proportional and derived coefficients, respectively, having units of seconds /°C difference between the set-point and measured boiler temperature.

Note: concerns modulated control of a single burner.

‘Difference starts burner’ is the boiler set-point to temperature measurement difference required to start burner control.

‘Initial burner control delay’ postpones burner control for a (short) period of time before boiler working starts.

‘Overall burner control time’ specifies the burner response time from fully closed to fully open (0 - 100%).

‘Minimum boiler ON time’ prevents short-cycling.

- 2. Use this setting to specify the maximum position of the burner during any programmed Auxiliary Period.

Burner position alarm

This function is typically used with WKK (Dutch) co-generation schemes, for which burner position and gas consumption monitoring are critical factors.

- 3. ‘Burner position deviation’ sets an alarm on the percentage difference (plus or minus) between the burner position and its set-point. Enter a positive value to enable the alarm, or ‘0’ to cancel the control function.

‘Burner alarm delay’ specifies a time delay before the alarm annunciates.

– Monitoring

If the boiler is ON, the reading displays the current burner set-point.

If the boiler is OFF, the reading displays current burner position, and the alarm is deactivated.

‘Burner position input n°’ allows a burner position sensor connected to a specific numbered input to be used for burner positioning control. Enter ‘0’ to cancel this function.

Recirculating or Auxiliary pump

- 4. The ‘Recirculating pump output n°’ setting specifies the dedicated MCU output for control of the pump. The output is ON while the boiler is working or if the boiler valve is open, otherwise operation is cyclical (hourly, see next setting). Enter ‘0’ to cancel the function.

‘Recirculating pump ON time’ defines the hourly ON time of the control output if the boiler is OFF or if the boiler valve is closed.

The ‘ON / OFF output no° (stop modul)’ setting specifies the number of a dedicated output associated with the end of boiler valve modulation. The output is OFF when the boiler valve is closed.

## Twin Firing Boiler

GENERAL    HEATING   BOILER   OTHER   FIRING

| ON/OFF controlled second burner Settings boiler 1 |  |  |  |  |  |  |  |  |  | 10 : 12 : 15 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| T diff. for high firing [ 0 – 50 °C ] Delay before starting [ 0 – 3600 sec ] Max permitted outside temp [ -25/+40 °C ] T° diff stops high firing [ 0 – 130 °C ] Time before return to normal firing [ 0 – 3600 sec ] Kp boiler (sec/ 1deg) [1 – 10 sec/1deg ] Kd boiler (sec/ 1deg) [1 – 10 sec/1deg ] Initial burner control delay [ 0 – 600 sec ] Overall burner control time [ 0 – 1200 sec ] |  |  |  |  |  |  | : : : : : : : : : | 5.0 5 8.0 |  |  |  | °C sec °C °C sec sec/°C sec/°C sec sec |
| BLR N° |  |  |  |  |  | MODIFY |  |  |  |  | QUIT |  |

1

2

3

- 1. ‘Temperature difference for high firing’ specifies the temperature offset below the boiler set-point required to start high firing.

The measured difference must exist for a time specified by ‘Delay before starting’.

Outside temperatures in excess of the maximum permitted value prevent high firing.

Two-stage modulated single burner

- 2. ‘Temperature difference stop high firing’ specifies the offset below the set-point at which high firing turns OFF (anticipating the temperature rise).

‘Time before return normal firing’ specifies a delay before the boiler returns to normal firing after stage 2 firing is turned OFF.

Note: modulation of the burner is based on boiler temperature during normal and high firing.

Modulated second burner

- 3. Kp and Kd are proportional and derived coefficients. The units are ‘seconds /°C difference’ between the boiler set-point and its temperature measurement.

‘Initial burner control delay’ postpones burner control for a (short) period of time before the boiler starts.

‘Overall burner control time’ specifies the burner response time from fully closed to fully open (0 – 100%).

## Special Operating Modes

GENERAL    HEATING    BOILER    OTHER    VARIOUS

| By way of an example, an Auxiliary Period could be set up for reduced daytime or standby mode working. Settings boiler 1 |  |  |  |  |  |  |  |  |  | 10 : 12 : 15 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Start of auxiliary period [ 00:00 – 23:59 ] End of auxiliary period [ 00:00 – 23:59 ] Auxiliary period boiler temp [ 0 – 130 °C ] Close boiler valve during aux per [ Yes / No ] Close valve boiler deactivated [ Yes / No ] |  |  |  |  |  |  | : : : : : | 11:00 15:00 60.0 NO NO |  |  |  | °C |
| BLR N° |  |  |  |  |  | MODIFY |  |  |  |  | QUIT |  |

1

2

- 1. One period (start – end) includes a specific boiler temperature set-point, and the option to close the boiler valve.

Note: the boiler set-point must be > minimum water temperature.

- (2) If ‘Close valve boiler deactivated’ = ‘‘Yes’, the boiler valve is closed when the boiler is not on line.

# HEATING TRANSPORT LINES

- Environmental influences: outside temperature, frost, rain, and forced CO2.

- Heat buffering.

- Control of a 2nd pump.

## Setting up control

GENERAL    HEATING   TRANSPT

| The ‘Minimum / maximum water temperature’ settings define the control range. Settings transport 1 |  |  |  |  |  |  |  |  |  | 10 : 12 : 15 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Minimum water temperature [ 0 – 130 °C ] Maximum water temperature [ 0 – 130 °C ] Transport water temp increase [ 0 – 50 °C ] Water temperature alarm delay [ 0 – 120 min ] |  |  |  |  |  |  | : : : : | 35.0 60.0 10 10 |  |  |  | °C °C % min |
| TRANSPT |  |  |  |  |  | MODIFY |  |  |  |  | QUIT |  |

‘Transport water temp increase’ determines the transport set-point, a floating temperature that equals the highest heating loop request value increased by the entered  percentage.

The final setting specifies a delay before the transport temperature alarm annunciates.

## Influences

### Outside temperature

GENERAL    HEATING   TRANSPT

| 1. The two outside temperature settings define the range. Settings transport 1 |  |  |  |  |  |  |  |  |  | 10 : 12 : 15 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Outside T° for start of influence [ -25/+40 °C ] Outside T for max influence [ -25/+40 °C ] Max infl. on min water temp [ 0 – 130 °C ] Outside T° for start of influence [ -25/+40 °C ] Outside T for max influence [ -25/+40 °C ] Max infl. on min water temp [ -130/+130 °C ] Temperature sensor input number [ 0 – 256 ] Water T° increase, forced CO2 [ 0 – 100 % ] Time start frost heating [ 00:00 – 23:59 ] Time end frost heating [ 00:00 – 23:59 ] O/s T° activate function [ -25/+40 °C ] Heating temperature [ 0 – 130 °C ] Heating ON, rain detected [ Yes / No ] |  |  |  |  |  |  | : : : : : : : : : : : : : | 8.0 0.0 10 |  |  |  | °C °C °C °C °C °C % °C °C |
| TRANSPT |  |  |  |  |  | MODIFY |  |  |  |  | QUIT |  |

1

2

3

4

‘Max. influ. on min. water temp.’ specifies the number of degrees increase in the minimum water temperature at maximum influence. The effect is proportional over the range.

- 2. As above but (a) the influence can be a +ve or –ve entry, and (b) the reference measurement is a sensor identified by a numbered input ( 0 – 256).

### Forced CO2 heat storage

    - 3. Increasing the transport set-point by the percentage entered allows surplus heat to be buffered under forced CO2 working conditions. Enter sufficient increase to allow the transport to reach a temperature near maximum.

### Frost and snow influence

Snow detection = frost + rain detected.

- 4. The influence is activated during the specified (start – end) period when the outside temperature falls below the ‘O/s T° activate function’ threshold.

The ‘Heating temperature’ specifies the transport set-point under the influence.

If ‘Heating ON, rain detected’ = Yes, the influence is only activated by rain.

## Hot Water Storage

GENERAL    HEATING    TRANSPT

| Storing heat can reduce energy consumption at peak times and prevent boiler short-cycling. Settings transport 1 |  |  |  |  |  |  |  |  |  | 10 : 12 : 15 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Storage starts [ 00:00 – 23:59 ] Storage ends [ 00:00 – 23:59 ] Number degrees of storage [ -130/+130 °C ] Storage interval [ 0 – 1200 min ] Storage starts [ 00:00 – 23:59 ] Storage ends [ 00:00 – 23:59 ] Number degrees of storage [ -130/+130 °C ] Storage interval [ 0 – 1200 min ] |  |  |  |  |  |  | : : : : | 04h00 05:00 10 12 19:00 20:00 10 12 |  |  |  | FT FT °C min °C min |
| TRANSPT |  |  |  |  |  | MODIFY |  |  |  |  | QUIT |  |

1

2

- 1 & 2. Two periods of storage (start – end) are possible.

‘Number degrees of storage’ is a floating offset temperature (+ve or –ve) applied to the transport set-point at the start of the period.

‘Storage interval’ specifies the time to reach the final storage temperature, which is then maintained until the period ends.

## Configuration

GENERAL    HEATING    TRANSPT    OTHER     TPT CFG

| Mixing Valve Control Settings transport 1 |  |  |  |  |  |  |  |  |  | 10 : 12 : 15 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Temp diff. to control 3WV pos [ 0 –10 °C ] 3WV control time per degree C [ 0 – 120 sec ] 3WV overall control time [ 0 – 1200 sec ] Heating pump on, water temp [ 0 –130 °C ] Stop pump (Economy) [ Yes / No ] Pump and 3WV service interval [ 0 – 500 h ] 3WV control interval [ 1 – 60 min ] Diff (Tamb,Tventil) stops pump [ -50/+50 °C ] Open 3WV at blr T° opens 3WV [ Yes / No ] Min. position 3WV [ 0 – 100 % ] Input number for position 3WV [ 1 – 256 ] Transport T° activate 2nd pump [ -130/+130 °C ] Delay before pump stops [ 0 – 900 min ] Return T° activates 2nd pump [ Yes / No ] Temp diff. starts 2nd pump [ -130/+130 °C ] Minimum ON time [ ] Switch pump 1 /2 [ Yes / No ] Pump interval 1 /2 [ 0 – 30000 sec ] |  |  |  |  |  |  | : : : : | 2.0 2 120 0.5 YES 120 4.0 NO 0 YES 10.0 NO |  |  |  | °C sec sec °C h min °C % °C min °C min sec |
| TRANSPT |  |  |  |  |  | MODIFY |  |  |  |  | QUIT |  |

1

2

3

4

5

- (1): ‘T° diff. to control 3WV’ specifies the temperature difference (measurement – set-point) needed for regulation to start.

‘3WV control time per °C’ specifies the time based control  rate for the valve.

‘Overall control time’ specifies the response time from fully closed to fully open (0 – 100%).

Transport pump control

- 2. ‘Heating pump on water t°’ specifies the pipe temperature difference (measurement – set-point) needed to start the pump.

If ‘Stop pump (Economy)’ = Yes, providing the pipe temperature > set-point the pump will turn OFF when the heating pumps stop.

The control interval (or control cycle) applies to both the pump and mixing valve.

‘Diff (Tamb,Tventil) stops pump’: specifies the difference between the ambient temperature measurement and the ventilation temperature set-point that causes the pump to turn OFF.

Note: to cancel, enter a value > 40.0 °C.

Safety positions

- (3): If ‘Open 3WV at blr T° opens 3WV’ = Yes, control opens the mixing valve automatically if the boiler temperature reaches the safety threshold that causes all heating loop mixing valves to open.

‘Minimum position 3WV’ specifies a minimum position for the mixing valve.

If a mixing valve position sensor is fitted it must be allocated to a numbered input (note: the sensor output signal must be compatible with the controller).

2nd transport pump

- 4. The ‘Transport T° activate 2nd pump’ setting can have either a positive or a negative entry.

+ve entry: the pump turns ON when the transport set-point > the entered temperature

–ve entry: the pump turns ON when the transport set-point > the minimum water temperature by an amount equal to the absolute value of the entered temperature.

When the starting conditions are no longer valid, the pump stops once the ‘Delay before pump stops’ time has elapsed.

– Control based on the transport return temperature

‘Return T° activates 2nd pump’ = Yes enables this function.

‘Temp diff starts 2nd pump’ specifies the difference between the transport set-point and the return pipe temperature that turns the pump ON.

‘Minimum pump ON time’ is used to prevent short-cycling.

Switch over between two pumps

- 5. The ‘Switch pump 1 /2’ = Yes enables this function.

‘Pump interval 1 /2’ specifies the changeover between the pumps.

### Temperature Sensor Configuration

GENERAL    HEATING    TRANSPT    OTHER     TPT CFG

| Where the transport consists of an in-line buffer pool several sensors may be required in order obtain a meaningful temperature measurement. Settings transport 1 |  |  |  |  |  |  |  |  |  | 10 : 12 : 15 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Measurement percentage, sensor n°1 [ 0 – 100 % ] Measurement percentage, sensor n°2 [ 0 – 100 % ] Measurement percentage, sensor n°3 [ 0 – 100 % ] |  |  |  |  |  |  | : : : | 40 30 30 |  |  |  | % % % |
| TRANSPT |  |  |  |  |  | MODIFY |  |  |  |  | QUIT |  |

- Each sensor contributes a percentage of the measurement relative to the total size of the transport.

# CO2 DOSING

- 3 sources of CO2: free, forced and liquefied.

- 4 possible daily periods.

- Solar radiation, wind and vent influences.

Injections of free CO2 can occur under normal conditions when the boiler is ON for heating. Forced CO2 working generates the temperature increases (boiler, heating, transports) necessary to force the boiler ON for CO2.

## Setting up control

COMPART   OTHER    OTHER   CO2

| 1. The 4 daily dosing periods must not overlap and should end before midnight. Settings CO2 compartment 1 |  |  |  |  |  |  |  |  |  | 10 : 12 : 15 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Enable CO2 injections [ Yes / No ] Start time [ 00:00 – 23:59 ] Start time [ 00:00 – 23:59 ] Start time [ 00:00 – 23:59 ] Start time [ 00:00 – 23:59 ] End time [ 00:00 – 23:59 ] Min CO2 level activate alarm [ 0 – 20000 ppm ] Max CO2 level activate alarm [ 0 – 20000 ppm ] Free CO2 threshold [ 0 – 20000 ppm ] Free CO2 threshold [ 0 – 20000 ppm ] Free CO2 threshold [ 0 – 20000 ppm ] Free CO2 threshold [ 0 – 20000 ppm ] Forced CO2 threshold [ 0 – 20000 ppm ] Forced CO2 threshold [ 0 – 20000 ppm ] Forced CO2 threshold [ 0 – 20000 ppm ] Forced CO2 threshold [ 0 – 20000 ppm ] Liquefied CO2 threshold [ 0 – 20000 ppm ] Liquefied CO2 threshold [ 0 – 20000 ppm ] Liquefied CO2 threshold [ 0 – 20000 ppm ] Liquefied CO2 threshold [ 0 – 20000 ppm ] Min deficit for injection [ 0 – 50 mBar ] Max deficit for injection [ 0 – 50 mBar] Max injection time [ 0 – 1400 min ] CO2 measurement sample time [ 0 – 1200 sec ] Heating water temp increase [ 0 – 100 % ] Stop free CO2, use for forcing [ Yes / No ] Maximum permitted temperature [ -10/+40 °C ] Min OFF time, liquid CO2 inj. [ 0 – 1400 min ] Max injection time, liquid CO2 [ 0 – 1400 min ] Minimum ON time [ 0 – 1400 min ] Minimum OFF (pause) time [ 0 – 1400 min ] |  |  |  |  |  |  | : : : : : : : : : : : : : : : : : : : | YES 10:00 19:00 200 1400 600 300 0.5 9.5 10 60 10 NO 28.0 10 5 5 |  |  |  | ppm ppm ppm ppm ppm ppm ppm ppm ppm ppm ppm ppm ppm ppm mBar mBar min sec % °C min min min min |
|  |  |  |  | OTHER |  | MODIFY |  |  |  |  | QUIT |  |

1

2

3

4

5

6

The minimum and maximum CO2 alarm thresholds apply throughout the day.

Note: for the alarm to be effective and workable the limits should not be set at the extremes of the sensor range.

Each period can be assigned different injection thresholds for free, forced and liquefied CO2.

Note: the liquefied CO2 threshold is independent of the boiler status.

- 2. Injections are conditional on the saturation deficit being within the min / max range.

3. The ‘Max injection time’ setting limits the duration of a single injection. It also specifies the duration of a single injection of liquefied CO2. Vent influence may increase the entered value (see later on).

The ‘CO2 measurement sample time’ specifies the time taken for a CO2 scanner / analyzer set to pump air samples from the compartment: adjust the value according to the distances involved.

- 4. ‘Heating water temp increase’ allows the set-point temperatures of heating loops 1 and 2 to be increased in order to dissipate excess heat during forced CO2 production. Use this setting if there is no buffer tank facility.

Injections of free CO2 can be stopped in favor of using the flue gas for compartments calling for forced CO2.

Specify a ‘Maximum permitted temperature’ above which requests for CO2 are ignored, or enter ‘0’ to cancel this setting.

- 5. Set minimum OFF and maximum injection times for liquefied CO2 dosing.

- 6. To avoid short-cycling specify ‘Minimum ON /OFF times’ to maintain the CO2 request status of the compartment.

## Various Influences

### Solar radiation

COMPART   OTHER    OTHER   CO2    OTHER   RAD INF

| 1. Specify minimum and maximum limits to define the influence range. Outside influences on CO2 compartment 1 |  |  |  |  |  |  |  |  |  | 10 : 12 : 15 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Rad. for minimum influence [ 0 – 1000 W/m² ] Rad. for maximum influence [ 0 – 1000 W/m² ] Max infl. on free CO2 threshold [ 0 – 20000 ppm ] Max infl. on forced CO2 threshold [ 0 – 20000 ppm ] Max infl. on liquid CO2 threshold [ 0 – 20000 ppm ] Wind speed for minimum influence [ 0 – 72 km/h ] Wind speed for maximum influence [ 0 – 72 km/h ] Max infl. on free CO2 threshold [ 0 – 20000 ppm ] Max infl. on forced CO2 threshold [ 0 – 20000 ppm ] Max infl. on liquid CO2 threshold [ 0 – 20000 ppm ] Vent position for min. influence [ 0 – 100 % ] Vent position for max. influence [ 0 – 100 % ] Max infl. on free CO2 threshold [ 0 – 20000 ppm ] Max infl. on forced CO2 threshold [ 0 – 20000 ppm ] Max infl. on liquid CO2 threshold [ 0 – 20000 ppm ] |  |  |  |  |  |  | : : : : : : : : : : : : : : : | 400 700 600 100 |  |  |  | W/m² W/m² ppm ppm ppm km/h km/h ppm ppm ppm 100% 100% ppm ppm ppm |
|  |  |  |  |  |  | MODIFY |  |  |  |  | QUIT |  |

1

2

3

Specify the maximum influence (increase or decrease) on each of the CO2 thresholds. The influence is proportional over its range

Note: where the strategy for optimizing CO2 depends primarily on sunlight use of the solar radiation influence is recommended.

### Wind speed

    - 2. The range and maximum influence parameters are the same as for solar radiation.

### Vent

    - 3. The parameters are identical to 1. and 2.

### Vent influences

COMPART   OTHER    OTHER   CO2    OTHER    VNT INF

| Reduction of vent opening Outside influences on CO2 compartment 1 |  |  |  |  |  |  |  |  |  | 10 : 12 : 15 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| CO2 level start influence [ 0 – 20000 ppm ] CO2 level maximum influence [ 0 – 20000 ppm ] Max infl on max vent pos,lee [ 0 – 100 % ] Max infl on max vent pos, wind [ 0 – 100 % ] CO2 influ. on max vent pos [ Yes / No ] Max vent pos during inject. [ 0 – 100 % ] Time maintain max. vent position [ 0 – 900 min ] Min wind speed influence [ 0 – 72 km/h ] Max wind speed influence [ 0 – 72 km/h ] Max infl. on max pos, for CO2 [ 0 – 100 % ] Max vent pos stops forced CO2 [ 0 – 100 % ] Max influ. vent pos max inj time [ 0 – 100 % ] Max infl. max inj. time, blr CO2 [+/- 30000 sec] Max infl. on max inj. time, liq. CO2 [+/- 30000 sec] |  |  |  |  |  |  | : : : : : : : : : : : : : | 500 200 10 30 NO 30 15 15 35 15 40 30 15 10 |  |  |  | ppm ppm % % % min Km/h Km/h % % % sec sec |
|  |  |  |  |  |  | MODIFY |  |  |  |  | QUIT |  |

1

2

3

4

- 1. Specify the CO2 concentration levels (start – maximum) for the limits of the influence.

Note: these limits act independently of the threshold levels for free / forced injections.

Specify the maximum reduction of the lee and windward vents at maximum influence.

Reduction of maximum vent position: forced CO2 working

Note: if this function is enabled the settings in 1. above have no effect.

- 2. To enable the function set ‘CO2 influ. on max vent pos’ = Yes, and specify a maximum vent opening during injections.

Specify the time that the vent remains at the entered maximum position.

Specify a min – max influence range over which wind speed reduces the maximum position.

Fix the maximum amount of reduction due to the influence of wind.

Vent position cancels forced CO2

Note: this influence is active only if ‘CO2 influ. on max vent pos’ = No.

- 3. The ‘Max pos stops forced CO2’ setting fixes a vent maximum position above which forced CO2 working is canceled (including the associated temperature increases) due to high temperature conditions in the compartment.

Increase maximum injection time with vent opening

- 4. The ‘Max influ. vent pos. max inj time’ setting specifies the position of the vent at which the influence on maximum injection time is greatest.

The remaining two settings fix the maximum increases on boiler and liquefied CO2 injection times. The influence is proportional to the vent position.

Note: new injection time = Maximum injection time +Increase due to the vent opening.

## General Settings

GENERAL    HEATING    CO2

| Applying to all compartments. Settings CO2 general |  |  |  |  |  |  |  |  |  | 10 : 12 : 15 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Enable CO2 injections [ Yes / No ] Minimum injection time [ 0 – 1440 min ] Delay before CO2 valve opens [ 0 – 1440 min ] Maximum injection time [ 0 – 1440 min ] Enable alarm (CO) [ Yes / No ] Pos valve liquid CO2 boiler ON [ 0 – 100 % ] Overall valve control time [ 0 – 1200 sec ] |  |  |  |  |  |  | : : : : : : : | YES 1 5 10 YES 60 210 |  |  |  | min min min % sec |
|  |  |  |  | OTHER |  | MODIFY |  |  |  |  | QUIT |  |

- Enable injections of CO2.

- Specify a minimum CO2 valve OPEN time (to prevent short-cycling)

- Specify a delay between the boiler starting and the beginning of injections.

Note: this is intended to reduce the possibility of injections of carbon monoxide (CO) occurring at the start of combustion.

- Enable the recording of CO alarms (only effective if detection is implemented via an MCU input).

- Specify the position of a mixing valve that combines liquefied and boiler CO2 circuits.

Enter the mixing valve response time from fully closed to fully open (0 – 100%).

## Configuration

GENERAL    HEATING    CO2    CFG.CO2

| Applying to all compartments. Settings CO2 general |  |  |  |  |  |  |  |  |  | 10 : 12 : 15 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| CO2 measurement sample time [ 0 – 1200 sec ] PPM increase halts injections [ 0 – 20000 ppm ] No. comparts requesting CO2 [ 1 – n° compart ] Boiler water T° increase [ 0 – 100 % ] |  |  |  |  |  |  | : : : : | 90 90 2 10 |  |  |  | sec ppm % |
|  |  |  |  |  |  | MODIFY |  |  |  |  | QUIT |  |

- Specify the time taken for a CO2 scanner / analyzer set to pump air samples from outside the greenhouse: adjust the value according to distance.

- The ‘PPM increase stops injections’ setting defines a control margin above the set-point thresholds at which injections stop.

- ‘No comparts requesting CO2’ specifies how many compartments must be requesting CO2 in order to activate forced CO2 working. The boiler set-point is increased forcing it to produce CO2 together with extra heat, which must be stored.

- The ‘Boiler water T° increase’ setting specifies the amount of increase applied for forced CO2 working.

Note: an increase of 100% means the boiler will reach its maximum working temperature, producing a useful amount of heat for storage. In the absence of a buffer, program an increase at least large enough to force the boiler to work for CO2.

# FORCED AIR HEATING

- Maintain ambient temperature.

- Select an alternative temperature reference (e.g. ground temperature).

- Use for cooling.

- Solar radiation, CO2 and humidity influences.

## Setting up control

COMPART    HEATING    FCD AIR

| Ambient temperature Heating settings comp 1 |  |  |  |  |  |  |  |  |  | 10 : 12 : 15 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Fcd air htg n° 1, 07:10R / 17:30S (2) |  |  |  |  |  |  |  |  |  |  |  |  |
| Start temperature [ -10/+40 °C ] Stop temperature [ -10/+40 °C ] |  |  |  |  |  |  | : : : | 16.0 17.0 |  |  |  | °C °C |
| HTG TYP |  | PERIODS |  |  |  | MODIFY |  |  |  |  | QUIT |  |

- The ‘Start temperature’ is the effective temperature set-point for starting the fan. Above the ‘Stop temperature’ the fan turns off.

Note: if ambient temperature is not to be the reference, select the set-point values accordingly (see Configuration).

## Configuration

COMPART    HEATING    FCD AIR   OTHER     CONFIG

| 1. Fan working obeys the minimum ON and OFF times irrespective of ambient temperature changes: e.g., the fan stays OFF for the minimum time even if the ambient temperature falls below the set-point. Influences on heating comp 1 |  |  |  |  |  |  |  |  |  | 10 : 12 : 15 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Fcd air htg n° 1 |  |  |  |  |  |  |  |  |  |  |  |  |
| Minimum ON time [ 0 – 60 min ] Minimum OFF time [ 0 – 60 min ] Forced air control T° input [ 0 – 256 ] Cooling [ Yes / No ] Temperature sensor [ T1, T2, T1/T2 ] CO2 measurement sample time [ 0 – 1200 sec ] |  |  |  |  |  |  | : : : : : : : | 3 2 0 NO T1 60 |  |  |  | mn mn sec |
| HTG TYP |  |  |  |  |  | MODIFY |  |  |  |  | QUIT |  |

1

2

3

- 2. This setting specifies the number of a physical input to be used as the temperature reference for the fan.

Note: in this case choose appropriate set-point values (see §13.1above) in keeping with the temperature reference. The default entry of ‘0’ selects ambient temperature as the reference.

- 3. If ‘Cooling’ = ‘Yes’, the fan turns ON when the ambient temperature is greater than the set-point, and vice versa.

If two sensor shelters are present, select the source of the temperature measurement: that is, T1, T2 or T1/T2 for the average of both.

Enter the time taken for a CO2 scanner/analyzer set to pump air samples from the compartment.

## Influences

### Solar radiation

COMPART    HEATING    FCD AIR   OTHER     RAD INF

| 1. Specify the minimum and maximum limits defining the influence range for direct solar radiation. Influences on heating comp 1 |  |  |  |  |  |  |  |  |  | 10 : 12 : 15 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Fcd air htg n° 1 |  |  |  |  |  |  |  |  |  |  |  |  |
| Rad. for minimum influence [ 0 – 1000 W/m² ] Rad. for maximum influence [ 0 – 1000 W/m² ] Max influence on start/stop T° [ -40/+40 °C] Accumul. radiation start influ. [0 -10000 Wh/m² ] Accumul. radiation for max influ. [0 -10000 Wh/m² ] Max influence on start/stop T° [ -40/+40 °C] Time influence starts [ 00:00 – 23:59 ] Time influence ends [ 00:00 – 23:59 ] |  |  |  |  |  |  | : : : : : : : : | 200 400 -2.0 1500 2500 1.0 0 -120 |  |  |  | W/m² W/m² °C Wh/m² Wh/m² °C SS SS |
| HTG TYP |  |  |  |  |  | MODIFY |  |  |  |  | QUIT |  |

1

2

3

Specify the maximum influence (+ve or -ve) on the start / stop temperatures. The influence is proportional over its range

- 2. Specify the range and influence settings for accumulated solar radiation.

- 3. Define a period of activation for the influence.

### Assisted CO2 working

COMPART    HEATING    FCD AIR   OTHER     CO2 INF

| 1. Enable the influence and define its period of activation (start – end). Forced air for CO2 comp 1 |  |  |  |  |  |  |  |  |  | 10 : 12 : 15 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Forced air n° 1 |  |  |  |  |  |  |  |  |  |  |  |  |
| Enable forced air for CO2 [ Yes / No ] Start time [ 00:00 – 23:59 ] End time [ 00:00 – 23:59 ] CO2 level start fan assist [ 0 – 20000 ppm ] CO2 level stops fan assist [ 0 – 20000 ppm ] CO2 level suspends heating [ 0 – 20000 ppm ] Maximum temperature [ 0 – 50 °C ] |  |  |  |  |  |  | : : : : : : : | YES 08:00 16:30 200 450 2500 22.0 |  |  |  | ppm ppm ppm °C |
| HTG TYP |  |  |  |  |  | MODIFY |  |  |  |  | QUIT |  |

1

2

Specify the concentration levels to start and stop the fan.

Note: if forced air heating is already ON, fan operation for heating has priority during (and after) the period irrespective of the CO2 thresholds.

– Override thresholds

- 2. ‘CO2 level suspends heating’ defines a CO2 concentration level above which the forced air system stops even if the compartment temperature is too low. An entry of ‘3000 ppm’ ensures uninterrupted heating.

‘Maximum temperature’ defines a temperature threshold above which the forced air system stops even if CO2 concentration is too low.

### Humidity Influence

COMPART    HEATING    FCD AIR   OTHER     HUM INF

| Forced air heating is used to evacuate excess humidity. It turns OFF once humidity drops below the maximum permitted level. Forced air for humidity comp 1 |  |  |  |  |  |  |  |  |  | 10 : 12 : 15 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Forced air n° 1 |  |  |  |  |  |  |  |  |  |  |  |  |
| ON time [ 0 – 60 min ] ] OFF time [ 0 – 60 min ] Maximum temperature [ 0 – 130 °C ] |  |  |  |  |  |  | : : : | 22.0 |  |  |  | min min °C |
| HTG TYP |  |  |  |  |  | MODIFY |  |  |  |  | QUIT |  |

- Specify fan ON and OFF times to prevent short cycling.

- Specify the maximum permitted ambient temperature under this influence.

# SCREENS

- Three control modes: time-based, shade and thermal.

- Wind, outside temperature and heating influences (thermal screen).

## Time based control

COMPART    OTHER     SCREENS    FIX TIM

| 1. Enable time based control and define two periods of activation (per.1 and 2) during which the screen unfolds to the maximum specified length. Screen time settings comp 1 |  |  |  |  |  |  |  |  |  | 10 : 12 : 15 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Screen n° 1 |  |  |  |  |  |  |  |  |  |  |  |  |
| Operate at fixed times [ Yes / No ] Time screen unfolds, per 1 [ 00:00 – 23:59 ] Time screen folds, per 1 [ 00:00 – 23:59 ] Time screen unfolds, per 2 [ 00:00 – 23:59 ] Time screen folds, per 2 [ 00:00 – 23:59 ] Maximum length of screen [ 0 – 1000 cm ] Max permitted humidity [ 0 – 100 % ] Max permitted temperature [ -40/+40 °C] Fold, humidity exceeds max [ 0 – 1000 cm/% ] Fold, temperature exceeds max. [ 0 – 1000 cm/% ] Limit folding due to T and RH [ 0 – 1000 cm ] Rad. cancels influ. T and RH [ 0 – 1000 W/m² ] Start time [ 00h00 – 23h59 ] End time [ 00h00 – 23h59 ] O/s T° folds screen (thermal) [ -25/+40 °C ] |  |  |  |  |  |  | : : : : : : : : : : : : : : : | YES 18:00 22:00 11:00 14h00 600 95 28.0 3 4 30 0 |  |  |  | cm % °C cm/% cm/°C cm W/m² °C |
| SCRN No |  |  |  |  |  | MODIFY |  |  |  |  | QUIT |  |

1

2

3

- 2. Specify maximum permitted humidity and temperature thresholds: above these limits the screen begins to retract.

Specify retraction in units of cm/°C and cm/%, and fix a maximum amount of folding.

The ‘Rad cancels influ. T and RH’ setting can be used to specify a sunlight threshold below which the influence of T° and RH is disabled, for example to prolong darkness under slightly higher than normal T° and RH conditions.

- 3. Specify the start and end times for the time based period of operation.

Define an outside temperature threshold above which the screen folds.

## Shading control

COMPART    OTHER     SCREENS    SHADE

| 1. Enable control for shading and define a period of activation. Shade settings comp 1 |  |  |  |  |  |  |  |  |  | 10 : 12 : 15 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Screen n° 1 |  |  |  |  |  |  |  |  |  |  |  |  |
| Operate screen for shading [ Yes / No ] Time screen unfolds [ 00:00 – 23:59 ] Time screen folds [ 00:00 – 23:59 ] Radiation, shade length 1 [ 0 – 1000 W/m² ] Shade length 1 [ 0 – 1000 cm ] Radiation, shade length 2 [ 0 – 1000 W/m² ] Shade length 2 [ 0 – 1000 cm ] Radiation level folds screen [ 0 – 1000 W/m² ] Shade control folding delay [ ] Max permitted humidity [ 0 – 100 % ] Max permitted temperature [ -40/+40 °C] Fold, humidity exceeds max [ 0 – 1000 cm/% ] Fold, temperature exceeds max [ 0 – 1000 cm/°C ] Limit folding due to T and RH [ 0 – 1000 cm ] |  |  |  |  |  |  | : : : : : : : : : : : : : : | YES 09:00 16:00 600 420 400 210 100 5 95 28.0 3 4 30 |  |  |  | W/m² cm W/m² cm W/m² min % °C cm/% cm/°C cm |
| SCRN No |  |  |  |  |  | MODIFY |  |  |  |  | QUIT |  |

1

2

Specify two sunlight thresholds for unfolding and two corresponding screen lengths.

‘Radiation level folds screen’ defines a sunlight threshold below which low light causes the screen to fold.

The ‘Shade control folding delay’ setting causes the screen to wait after the command to fold (to L=0) becomes valid.

Note: the actual delay equals the entry value multiplied by the screen control interval (see §14.714.6).

- 2. Specify maximum permitted humidity and temperature thresholds: above these limits the screen begins to retract.

Specify retraction in units of cm/°C and cm/%, and fix a maximum amount of folding.

## Thermal Operation

COMPART    OTHER     SCREENS    THERMAL

| 1. Enable thermal control and define the night time activation period (start < midnight < end). Settings thermal screen comp 1 |  |  |  |  |  |  |  |  |  | 10 : 12 : 15 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Screen n° 1 |  |  |  |  |  |  |  |  |  |  |  |  |
| Thermal screen control [ Yes / No ] Start thermal period, night [ 00:00 – 23:59 ] O/s T unfolds screen, night [ -25/+40 °C ] Maximum length [ 0 – 1000 cm ] Time end thermal period [ 00:00 – 23:59 ] O/s T folds screen, day [ -25/+40 °C ] Radiation level folds screen [ 0 – 1000 W/m² ] Daytime rad. unfolds screen [ 0 – 1000 W/m² ] Daytime amb. T unfolds screen [ -40/+40 °C] Max permitted humidity [ 0 – 100 % ] Max permitted temperature [ -40/+40 °C] Fold, humidity exceeds max [ 0 – 1000 cm ] Fold, temperature exceeds max [ 0 – 1000 cm ] Limit folding due to T and RH [ 0 – 1000 cm ] Initial fold control distance [ 0 – 1000 cm ] Folding % increase per step [ 0 – 100 % ] Start normal folding at [ 0 – 1000 cm ] Fold if snow detected [ Yes / No ] Max inf on outside T°, unfolding [ -10/+40 °C ] Max inf on outside T°, folding [ -10/+40 °C ] Type of ambient T° [ 0, 1 ] |  |  |  |  |  |  | : : : : : : : : : : : : : : : : : : : : : | YES -10 8.0 450 10 2 100 10 95 28.0 3 4 30 5 20 350 YES |  |  |  | SS °C cm SR °C W/m² W/m² °C % °C cm/% cm/°C cm cm % cm |
| SCRN No |  |  |  | INFLUE. |  | MODIFY |  |  |  |  | QUIT |  |

1

2

3

4

5

Specify the temperature threshold below which the screen unfolds, and fix a maximum length.

Folding starts at the end of the period when outside temperature and sunlight exceed the thresholds.

Daytime safety settings.

- 2. Specify low sunlight and ambient temperature thresholds below which the screen unfolds again.

– ambient T° tracking

The temperature threshold can be a fixed value OR an offset (+ve or –ve) tracking the ambient temperature set-point: e.g. if entry = -1, then threshold = setp.T° - 1°C. The choice is conditioned by the ‘Type of ambient T°’ setting (see last setting).

- 3. Specify maximum permitted humidity and temperature thresholds: above these limits the screen begins to retract.

Specify retraction in units of cm/°C and cm/%, and fix a maximum amount of folding.

– ventilation T° tracking

Entering a negative offset for the temperature threshold will make it track the ventilation temperature set-point

E.g. if entry = -2, then threshold = setp. T° + 2°C (because the offset = the absolute value of the entry).

The folding process

- 4. Specify an ‘Initial fold control distance’ for the start of folding.

The ‘Folding increase per step’ setting determines the rate of folding, which increases progressively, as follows:

Let D= distance folded. Then, the amount of folding after each control interval is Dnew = Dold + %Dold.

Normal (continuous) folding starts when the screen reaches a length defined by the ‘Start normal folding at’ setting.

Specify whether the detection of snow causes the screen to fold to the limit fixed for excess T° and/or RH.

Wind influence on the outside temperature thresholds

- 5. Maximum wind speed influences on outside temperature thresholds for unfolding and folding.

- ‘Type of ambient T°’ (see 2. above): ambient temperature threshold can be a fixed value (entry = 0) or an offset tracking the ambient temperature set-point (entry =1).

Note: absence of compartment heating means no ambient temperature set-point, in which case the reference is ventilation temperature.

## Influences On Thermal Screen Folding

### Wind speed

COMPART    OTHER     SCREENS    THERMAL    INFLUE

| 1. The two wind speed settings define the influence range. Settings thermal screen comp 1 |  |  |  |  |  |  |  |  |  | 10 : 12 : 15 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Screen n° 1 |  |  |  |  |  |  |  |  |  |  |  |  |
| Wind speed for min influence [ 0 – 72 km/h ] Wind speed for max influence [ 0 – 72 km/h ] Influence on control interval [ 0 – 120 min ] Influence on % folding [ 0 – 100 % ] Reduction limit folding max T/H [ 0 – 1000 cm ] Outside T for min influence [ -25/+40 °C ] Outside T for max influence [ -25/+40 °C ] Influence on control interval [ 0 – 120 min ] Influence on % folding [ 0 – 100 % ] Reduction limit folding max T/H [ 0 – 1000 cm ] Htg T diff. for min influence [ -10/+20 °C ] Htg T diff. for max influence [ -10/+20 °C ] Influence on control interval [ 0 – 120 min ] Influence on % folding [ 0 – 100 % ] |  |  |  |  |  |  | : : : : : : : : : : : : : : | 10 30 2 10 8.0 2.0 2 10 1.0 10.0 2 10 |  |  |  | Km/h Km/h min % cm °C °C min % cm °C °C min % |
| SCRN No |  |  |  |  |  | MODIFY |  |  |  |  | QUIT |  |

1

2

3

Specify the maximum amount of influence on a). the ‘control interval’, b). the ‘folding increase per step’, and c). the limit on folding due to excess T° and/or RH. There is a reduction in each case, and the effect is proportional over the range.

### Outside temperature

    - 2. Identical to the wind speed influence.

### Heating

    - 3. The influence is proportional to difference between the high-temperature heating set-point and the minimum water temperature. The targets are the same as described in a) and b) above for the wind speed influence.

## Thermal Screen Influence On Heating Set-point

COMPART    OTHER     SCREENS   THERMAL   OTHER

| Specify the number of degrees to add or subtract when the screen unfolds. Settings thermal screen comp 1 |  |  |  |  |  |  |  |  |  | 10 : 12 : 15 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Screen n° 1 |  |  |  |  |  |  |  |  |  |  |  |  |
| Infl. on htg water T, unfold [ -90/+90 °C ] Infl. on htg water T, fold [ -90/+90 °C ] Influence on heating 1 [ Yes / No ] Influence on heating 2 [ Yes / No ] Influence on heating 3 [ Yes / No ] |  |  |  |  |  |  | : : : : : | 20.0 2.0 YES NO NO |  |  |  | °C °C |
| SCRN No |  |  |  |  |  | MODIFY |  |  |  |  | QUIT |  |

- Specify the number of degrees to add or subtract per control cycle (step) as the screen folds.

- Activate (or not) the influence on each heating loop set-point.

Note: where only high temperature and ground heating exist, heating 1 = high temperature loop and heating 2 = ground heating.

## General Settings

COMPART    OTHER     SCREENS    VARIOUS    GENERAL

| 1. Specify the screen control interval (or cycle), which defines the time between successive positional calculations. Settings thermal screen comp 1 |  |  |  |  |  |  |  |  |  | 10 : 12 : 15 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Screen n° 1 |  |  |  |  |  |  |  |  |  |  |  |  |
| Screen control interval [ 0 – 120 min ] Minimum correction length [ 0 – 1000 cm ] Maximum correction length [ 0 – 1000 cm ] Max variation, plus [ 0 – 1000 W/m² ] Max variation, minus [ 0 – 1000 W/m² ] |  |  |  |  |  |  | : : : : : | 2 5 50 20 30 |  |  |  | min cm cm W/m² W/m² |
| SCRN No |  |  |  |  |  | MODIFY |  |  |  |  | QUIT |  |

1

2

Note: this figure also determines the ‘Delay before folding’ (see §14.2).

Specify the smallest and greatest length corrections that can be applied over one control interval.

Staged response to light level variations (e.g. clouds)

- 2. Specify the maximum change (+ and – ) in the level of direct sunlight having an effect on the position of the screen.

## Configuring The Screen

COMPART    OTHER     SCREENS    VARIOUS   SCR CFG

| 1. Enter the measured time to unfold and fold the screen between 0% and 100%. Settings thermal screen comp 1 |  |  |  |  |  |  |  |  |  | 10 : 12 : 15 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Screen n° 1 |  |  |  |  |  |  |  |  |  |  |  |  |
| Control time to fold [ 0 – 1800 sec ] Control, time to unfold [ 0 – 1800 sec ] Control folding distance [ 0 – 1000 cm ] Control motor delay [ sec ] Minimum length, rain detected [ 0 – 1000 cm ] Minimum length, storm detected [ 0 – 1000 cm ] No of screen to track (master) [ 1 – n° comp. ] Comp number of master screen [ 1 – n° comp. ] Track light in compartment n° [ 1 – n° comp.] Time after end stop [ 0 – 300 sec ] Minimum positional control [ 0 – 2000 ms ] Alarm delay [ 0 – 1440 sec ] |  |  |  |  |  |  | : : : : : : : : : : : : | 240 250 2 0 0 2 0 0 0 |  |  |  | sec sec cm sec cm cm sec x10ms sec |
| SCRN No |  |  |  |  |  | MODIFY |  |  |  |  | QUIT |  |

1

2

3

4

5

6

Enter the distance traveled between 100 % unfolded and  0% folded.

Specify the motor ‘backlash’ control time applying before the start of thermal screen folding.

- 2. Specify minimum screen lengths for rain or storm conditions.

- 3. For a ‘follow on’ (tracker) screen, specify the screen and compartment numbers of the leading screen.

- 4. Specify the motor ‘backlash’ control time that ensures full opening /closure of ‘Rolling screens’.

Control mode switching (time -> position sensing)

- 5. Specify the minimum, time-based control time (> ‘0’) that causes screen control to take account of position sensing. The effective value equals the entry multiplied by 10: e.g. to obtain 0.5sec enter a value of 50ms.

In the above example, control times < 0.5sec are ignored.

- 6. Specify a delay for the screen positional alarm.

– Alarm conditions

‘Minimum positional control’ and ‘Minimum correction length’ (see General) are > ‘0’.

The difference (+ or -) between the calculated and measured positions > the minimum correction length

The error difference persists after the delay.

# CIRCULATION FAN

- ON triggers: ambient temperature and/or humidity, heating water set-point.

- Cyclic working possible.

- CO2 level trigger.

- Fix vent position for air changes.

## Setting Up Control

COMPART    OTHER     FANS

| Difference mode Fan settings comp 1 |  |  |  |  |  |  |  |  |  | 10 : 12 : 15 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Fan n° 1 |  |  |  |  |  |  |  |  |  |  |  |  |
| Enable fan operation [ Yes / No ] Temp. difference starts fan [ 0 – 40 °C ] Humidity diff. starts fan [ 0 – 50 % ] Heating water T starts fan [ 0 – 130 °C ] Start cyclic fan operation [ 0 – 1440 min ] ON time, cyclic operation [ 0 – 1440 min ] Minimum ON time [ 0 – 1440 min ] Maximum ON time [ 0 – 1440 min ] Minimum OFF (pause) time [ 0 – 1440 min ] Vent position stops fan [ 0 – 100 % ] CO2 level starts fan [ 0 – 20000 ppm ] CO2 Injection starts fan [ Yes / No ] Minimum vent position [ 0 – 100 % ] |  |  |  |  |  |  | : : : : : : : : : : | YES 1.5 6 55 60 30 10 15 30 32 250 YES 0 |  |  |  | °C % °C min min min min min % ppm % |
| TYPE |  |  |  |  |  | MODIFY |  |  |  |  | QUIT |  |

1

2

1

3

4

1. Specify the ambient temperature to set-point difference required to turn the fan ON.

Use the ‘TYPE’ key to select a +ve (>), -ve (<) or +/- (<>) difference, and to specify the source sensor shelter, i.e. T1 or T2 (second shelter)

Specify the relative humidity to control range mid-point difference (+/–) required to turn the fan ON.

Specify the ‘Heating water T° starts fan’ threshold. The fan will always turn ON if the heating water set-point exceeds the threshold.

Enter minimum ON and maximum ON and OFF times to prevent short-cycling.

IMPORTANT: enter ‘0’ for the two cyclic settings (see below).

Cyclic mode

- 2. The ‘Start cyclic fan operation’ setting determines the length of one operating cycle

Specify the fan ON time during the operating cycle.

IMPORTANT: enter ‘0’ for the two T° and/or RH difference settings.

Combined mode

Program both groups (difference and cyclic modes) of settings. The fan works cyclically until an environmental condition becomes valid.

Miscellaneous settings

– Vent and CO2 stop/start influence

- (3). ‘Vent position stops fan’ fixes a threshold above which the fan turns OFF.

‘CO2 starts fan’ fixes a concentration above which the fan turns ON. Enter ‘0’ to cancel.

– Air mixing / air changes

- (4) ‘CO2 injection starts fan’ = Yes will start the fan when the CO2 pump starts, and provides degree of air mixing.

Fixing a ‘Minimum vent position’ for the leeward vent while the fan is ON is useful for air changes.

Note: fan working can be influenced during fumigation.

# VENTILATION  FAN

- ON triggers: saturation deficit, ventilation temperature, CO2.

- Coordinate vents with fan.

- Additional output control.

## Setting up control

COMPART   OTHER    OTHER    OTHER   FAN

| 1. Enable the fan and define a period (start-end) of activation. Settings exhaust fan comp 1 |  |  |  |  |  |  |  |  |  | 10 : 12 : 15 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Enable fan operation [ Yes / No ] Start time [ 00:00 – 23:59 ] End time [ 00:00 – 23:59 ] Deficit starts fan [ -50 / +50 mBar ] Ventilation T° diff. starts fan [ 0 – 50 ] CO2 level starts fan [ 0 – 20000 ppm ] Minimum ON time [ 0 – 1440 min ] Minimum OFF (pause) time [ 0 – 1440 min ] Maximum ON time [ 0 – 1440 min ] Maximum vent position [ -100 / +100 % ] Minimum vent position [ 0 – 100 % ] Minimum outside deficit [ 0 – 50 mBar ] Maximum outside deficit [ 0 – 50 mBar ] Deficit triggers aux output [ 0 – 50 mBar ] Temp triggers aux output [ 0 – 50 °C ] Number of auxiliary output [ 0 – 256 ] Compartment number for vents [ 1 – no comp. ] Number of vent [ 1 – 8 ] |  |  |  |  |  |  | : : : : : : : : : : | YES 10:00 17:00 2.0 2.0 2000 10 5 30 100 10 0 0 |  |  |  | mBar °C ppm min min min % % mBar mBar mBar °C |
|  |  |  |  |  |  | MODIFY |  |  |  |  | QUIT |  |

1

2

3

4

5

Specify the saturation deficit threshold below which the fan turns ON.

Specify the offset from the ventilation temperature set-point above which the fan turns ON.

Specify the level of CO2 concentration above which the fan turns ON.

Enter the minimum ON / OFF times to prevent short-cycling, and a maximum ON time.

Note: fan working always starts with a pause (= OFF).

Fan working controls vents

- 2. Specify a ‘Maximum vent position’ applying while the fan is ON (+ve entry) or throughout the activation period (–ve entry).

See also 5 below.

Outside saturation deficit condition

- 3. The fan is ON only while the saturation deficit is within the specified min – max range.

Control of an auxiliary output

- 4. Specify the ambient temperature and saturation deficit thresholds above which the designated output is ON while the fan is ON. When the fan is OFF the output is OFF. To cancel one or both of these functions enter a value of ‘0’.

Assign the auxiliary output by selecting a number between 0 and 256 corresponding to an unused MCU output.

Associating vents

- 5. Specify the number of the compartment associated with the vent position settings (see 2 above). The default value of ‘0’ = the current compartment.

Specify the number of the vent associated with the fan, as follows:

– at any height, control always targets the leeward vent of a double vent pair, and

– a single vent at any height is always controlled even when windward facing.

Note: if several fans are active the highest ‘Minimum vent position’ has overall effect.

Enter ‘0’ to deactivate the vent influence.

IMPORTANT: the value of the last setting MUST be ‘0’ if the fan is not enabled.

# LIGHTING

- Cyclical control based on solar radiation

- Assimilation lighting.

## Setting up cyclic control

COMPART   OTHER    OTHER    LIGHTING

| 1. Enable lighting and define two periods of cyclical control. Lighting settings comp 1 |  |  |  |  |  |  |  |  |  | 10 : 12 : 15 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Enable lighting cycle [ Yes / No ] Period 1 starts [ 00:00 – 23:59 ] Lighting ON time [ 0 – 1200 min ] Lighting OFF (pause) time [ 0 – 1200 min ] Period 1 ends [ 00:00 – 23:59 ] Period 2 starts [ 00:00 – 23:59 ] Lighting ON time [ 0 – 1200 min ] Lighting OFF (pause) time [ 0 – 1200 min ] Time cyclic ends [ 00:00 – 23:59 ] Rad. activates lighting [ 0 – 1000 W/m² ] Rad. deactivates lighting [ 0 – 1000 W/m² ] Amb. temp. deactiv. lighting [ 0 – 40 °C ] Enable cascade lighting [ Yes / No ] |  |  |  |  |  |  | : : : : : : : : : : | YES 16:00 20 20 19:59 20:00 40 40 23:00 50 100.0 30.0 NO |  |  |  | min min min min min W/m² W/m² °C |
|  |  |  |  |  |  | MODIFY |  |  |  |  | QUIT |  |

1

2

3

Specify separate ON and OFF times for each period (note: lighting is always OFF at the start).

- 2. Specify the solar radiation thresholds to turn lighting ON (activate) and OFF (deactivate).

Specify the ambient temperature threshold at and above which lighting control is inhibited.

- 3. If cascade is enabled, control turns each row of lamps ON and OFF in sequence.

## Assimilation Lighting

COMPART   OTHER    OTHER    LIGHTING    NEXT

| Direct solar radiation (stage 1) Lighting settings comp 1 |  |  |  |  |  |  |  |  |  | 10 : 12 : 15 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Enable lighting [ Yes / No ] Start time [ 00:00 – 23:59 ] Radiation activates lighting [ 0 – 1000 W/m² ] Radiation deactivates lighting [ 0 – 1000 W/m² ] Minimum ON time [ 0 – 1440 min ] Minimum OFF (pause) time [ 0 – 1440 min ] Max permitted temperature [ 0 – 40 °C ] End time [ 00:00 – 23:59 ] Interval between lighting ctl [ 0 – 1440 min ] Light assimilation set-point [ 0– 20000Wh/m²] Time end accumul. radiation [ 00:00 – 23:59 ] Theoretical W/m2 figure [ 0 – 1000 W/m² ] Amb. temp diff. lighting ON [ -40/+40 °C] Amb. temp diff. lighting OFF [ -40/+40 °C] Lighting OFF delay [ ] Lighting ON delay [ ] Sensor type [ 0,1 ] |  |  |  |  |  |  | : : : : : : : : : : | YES 16:00 50 100 20 10 28.0 20:00 20 2400 23:00 50 10.0 3.0 0 |  |  |  | W/m² W/m² min min °C Wh/m² W °C °C min min |
|  |  |  |  |  |  | MODIFY |  |  |  |  | QUIT |  |

1

2

3

4

- 1. Enable assimilation lighting and define the activation period (start – end).

- Specify the solar radiation thresholds to turn lighting ON (activate) and OFF (deactivate).

Enter minimum ON / OFF times to prevent short-cycling.

Specify the ambient temperature threshold at and above which lighting control is inhibited.

Light accumulation (stage 2)

- 2. Specify an interval after stage 1 ends.

The ‘Light assimilation set-point’ specifies the daily amount of light needed by the crop.

‘Time end accumul. radiation’ defines the end of assimilation lighting control (= end of stage 2, but see below)

The ‘Theoretical W/m² figure’ setting specifies the amount of light delivered by the strips, which is used to calculate the total amount of lighting supplied over stages 1 and 2.

IMPORTANT: since the light accumulation count begins at the start of stage 1, the light sum may reach the assimilation set-point at any time during the stage 1  stage 2 period: at this point assimilation lighting control ends.

Assimilation lighting based on ambient temperature

- 3. Specify the difference between the ambient temperature and the set-point to turn lighting ON (T°amb > setp.) and OFF (T°amb < setp.).

Miscellaneous settings

- 4. Specify the time delays that elapse before the lighting turns OFF and ON in response to solar radiation.

The ‘Sensor type’ settings selects the source of the solar radiation reading: that is, the weather station solarimeter (entry = 0) or the solarimeter in the compartment (entry = 1).

# ROOF SPRINKLERS

- Ambient temperature, saturation deficit and frost triggers

- Solar radiation, wind speed and rain overrides

## Setting up control

COMPART  OTHER  OTHER  OTHER  SPRINKL

| 1. Enable the function and define a period (start-end) of activation together with the required ON and OFF times. Settings sprinklers compartment n°1 |  |  |  |  |  |  |  |  |  | 10 : 12 : 15 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Enable roof sprinklers [ Yes / No ] Start time [ 00:00 – 23:59 ] End time [ 00:00 – 23:59 ] ON time [ 0 – 1200 min ] OFF time [ 0 – 1200 min ] Amb. T° start sprinklers [ 0 – 40 °C ] Deficit start sprinklers [ 0 – 50 mBar ] Radiation enable sprinklers [ 0 – 1000 W/m² ] Max vent pos sprinklers ON [ 0 – 100 % ] Wind speed stop sprinklers [ 0 – 72 km/h ] Stop if rain detected [ Yes / No ] Start if frost detected [ Yes / No ] Number of compartment to follow [ 1 – n° comps ] |  |  |  |  |  |  | : : : : : : : : : : | YES 12:30 16:30 1 1 22 5 300 100 20 NO NO Comp |  |  |  | min min °C mBar W/m² % km/h current n |
|  |  |  |  |  |  | O K |  |  |  |  | QUIT |  |

1

2

3

4

2. Specify the ambient temperature and saturation deficit thresholds above which the sprinklers turn ON.

Specify a solar radiation threshold below which the sprinklers are inhibited.

Specify the maximum vent opening applying while the sprinklers are ON (see also ‘Compartments without sprinklers’ below).

Overrides

- 3. Specify a wind speed threshold above which sprinkler operation stops.

Specify if sprinkler operation is to stop if rain is detected.

Specify if sprinkler operation is to start if frost is detected.

Compartment without sprinklers

For a non-equipped compartment, set ‘Enable roof sprinklers’ = No if the maximum vent opening must still apply when the sprinklers are turned ON (by another compartment controlling a single, common pump).

Fix a maximum vent position (see 2 above).

- 4. Specify the number of an equipped compartment to be tracked for sprinkler operation.

Note: all other menu settings are inoperative and the compartment sprinkler output is not enabled.

# FOG SYSTEM

- Saturation deficit, ambient temperature and humidity triggers.

- Wind speed and solar radiation influences.

- Vent position.

## Setting up control

COMPART    HUMID    FOG

| 1. Enable the function and define a period (start-end) of activation together with the required ON and OFF times. Settings fog comp 1 |  |  |  |  |  |  |  |  |  | 10 : 12 : 15 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Enable fog system [ Yes / No ] Start time [ 00:00 – 23:59 ] End time [ 00:00 – 23:59 ] Fog ON time [ 0 – 30000 sec ] Fog OFF time [ 0 – 30000 sec ] Deficit starts fog [ 0 – 50 mBar ] Max deficit stops fog [ 0 – 50 mBar ] Temperature starts fog [ 0 – 40 °C ] Max pos vent allow fogging [ 0 – 100 % ] Max vent pos with fogging ON [ 0 – 100 % ] Time max wind influ. fog ON time [ +/- 1000 sec ] Radiation start influence [ 0 – 1000 W/m² ] Radiation max influence [ 0 – 1000 W/m² ] Time max rad. influ. OFF time [ +/- 1000 sec ] Fog cascade working [ Yes / No ] Humidity starts fog [ 0 – 100 % ] Humidity stops fog [ 0 – 100 % ] Type of ambient T° [ 0, 1 ] Min time maintain vent position [ 0 – 1440 min ] |  |  |  |  |  |  | : : : : : : : : : : : : : : : : : : : | YES 10:00 15:00 40 3 7.0 15.0 0.0 100 30 0 NO 60% 99% |  |  |  | sec min mBar mBar °C % % sec W/m² W/m² sec min |
|  |  |  |  |  |  | MODIFY |  |  |  |  | QUIT |  |

1

2

3

4

5

6

7

- 2. Specify the saturation deficit thresholds that turn fog ON and OFF.

Note: ‘Maximum deficit stops fog’ is a safety threshold: saturation deficit rising to this level probably indicates a malfunction.

Specify the temperature threshold above which fog turns ON.

‘Maximum pos vent allow fogging’ fixes a vent override position above which fog is inhibited.

‘Maximum vent position fog ON’ limits the vent position while the fog is ON.

Wind speed and solar radiation influences

- 3. The ‘Time max wind influ. fog ON time’ setting specifies the maximum increase in the fog ON time due to the influence of wind speed. The effect is proportional over the same range of wind influence as defined for the windward vent (see §7.2.2).

Specify the minimum (start) and maximum limits defining the influence range for solar radiation on the fog OFF time.

The ‘Time max rad influ. fog ON time’ setting specifies the maximum increase in the fog OFF time due to solar radiation.

Cascade working

- 4. If cascade is enabled, ON/OFF control passes sequentially to the various fog system valves.

Humidity control

- 5. Specify the threshold below which fog turns ON

Specify the maximum threshold above which fog triggered by humidity turns OFF.

- 6. Where there are two sensor shelters select T1 or T2, or T1/T2 for the average.

- 7. Minimum time duration the vent is held at the set-point (or maximum) position after fog turns OFF.

# FUMIGATION TREATMENT PERIOD

- Period includes three phases: before (ready), during (treat), and after (purge).

- Vent, heating, fan and screen influences.

## Setting up control

COMPART   OTHER    OTHER    PHYTO

| 1. Enable phytosanitory treatment and specify a treatment date. Alternatively, setting ‘Fix treatment date’ = ‘No’ sets up a daily schedule. Phytosan. settings comp 1 |  |  |  |  |  |  |  |  |  | 10 : 12 : 15 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Enable phytosan. treatment [ Yes / No ] Fix treatment date [ Yes / No ] Treatment date [ DD/MM/YY ] Start time [ 00:00 – 23:59 ] End time [ 00:00 – 23:59 ] Vent pos during treatment [ 0 – 100 % ] Min vent pos after treatment [ 0 – 100 % ] Time min pos after treatment [ 0 / 1440 min ] Max vent pos after treatment [ 0 – 100 % ] Time max pos after treatment [ 0 / 1440 min ] Heating min water temp increase [ -130 / +100 °C ] Max temperature permit treatment [ 0 – 50 °C ] Max pos vent if temp exceeds max [ 0 – 100 % ] Activate phytosan. o/p [ Yes / No ] Output activation time [ 0 / 1440 min ] Pause between during and after [ 0 / 1440 min ] |  |  |  |  |  |  | : : : : : : : : : : | YES 08/11/97 18:00 23:30 0 10 30 10 30 20 50 0 YES 45 15 |  |  |  | % % min % min °C °C % min min |
| INF FAN |  | INF CSR |  | OTHER |  | MODIFY |  |  |  |  | QUIT |  |

1

2

3

4

Specify the treatment period start and end times.

Vents

- 2. Fix the position of the vent during treatment (but also see 3). Specify a minimum vent position after treatment and the duration of this override.

Specify a maximum vent position after treatment and the duration of this override.

Heating

- 3. Use the ‘Heating min water temp. increase’ parameter to either raise the minimum water temperature (+ve entry) OR to fix a limit for maximum water temperature (-ve entry).

Note: this is not applicable to ground heating.

Specify the maximum permitted ambient temperature during treatment, and also the position the vent is forced to if this temperature is exceeded.

Output

- 4. If ‘Activate phytosan. output’ = Yes, the corresponding output is activated for the specified time, and a pause interval between the treatment and purge phases is programmable.

### Circulation fan operation

COMPART   OTHER    OTHER    PHYTO    INF FAN

| Enable the fan and program ON times for the treatment and purge phases. Phyto. Infl on fan comp 1 |  |  |  |  |  |  |  |  |  | 10 : 12 : 15 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Enable fan for phyto. [ Yes / No ] Fan ON time during treatment [ min ] Fan ON time after treatment [ min ] Stop fan during [ Yes / No ] Fan Pause time after treatment [ min ] Fan ON time before treatment [ min ] |  |  |  |  |  |  | : : : : : : | YES 30 20 NO |  |  |  | min min min min |
|  |  |  |  |  |  | MODIFY |  |  |  |  | QUIT |  |

Alternatively, use the ‘Stop fan during’ and ‘Fan pause time after treatment’ settings to inhibit the fan during these phases.

- Lastly, if enabled, the fan can be turned ON during the ‘ready’ phase before treatment begins.

### Screen operation

COMPART   OTHER    OTHER     PHYTO    SCN INF

| Specify the length of the screen during and after treatment, and the time it remains at the post treatment position. Phyto. Infl on fan comp 1 |  |  |  |  |  |  |  |  |  | 10 : 12 : 15 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Scr. length during treatment [ 0 / 1000 cm ] Scr. length after treatment [ 0 / 1000 cm ] Time screen after treatment [ 0 / 1440 min ] |  |  |  |  |  |  | : : : | 400 0 20 |  |  |  | cm cm min |
|  |  |  |  |  |  | MODIFY |  |  |  |  | QUIT |  |

## Summary

# GROUND COOLING

- Two possible operating modes: with or without regulation of the heating loop (pump and mixing valve).

- Compressor turns ON when a single loop requests cooling and OFF when all loops are below their cut-out temperatures.

The operating mode is selected in the configuration menu (see next page).

## Setting up control

COMPART    OTHER    OTHER    OTHER    COOLING

| 1. Enable the function and program an overall (start – end) period of activation. Configuration heating compartment 1 |  |  |  |  |  |  |  |  |  | 10 : 12 : 15 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Ground heating (3) |  |  |  |  |  |  |  |  |  |  |  |  |
| Enable ground cooling [ Yes / No ] Start time [ 00:00 / 23:59 ] End time [ 00:00 / 23:59 ] Minimum water temperature [ 0 – 30 °C ] Maximum water temperature [ 0 – 30 °C ] Delay bef. stop GC, if max wtr T° [ 0 – 1440 min ] Start temperature [ -25/+40 °C ] Stop temperature difference [ -25/+40 °C ] 3WV control time per °C [ 0 – 120 sec ] Max variation V3V per interval [ 0 – 100 % ] |  |  |  |  |  |  | : : : | YES 10:00 17:00 10 25 5 12 0.5 |  |  |  | FT FT °C °C °C min °C °C sec % |
| TYP HTG |  | CONFIG |  |  |  | MODIFY |  |  |  |  | QUIT |  |

1

2

3

4

5

- 2. The ‘Minimum water temperature’ setting is the low pipe temperature threshold below which ground cooling turns OFF.

Safeguards

- 3. The ‘Maximum water temperature’ setting fixes a pipe temperature threshold above which ground cooling turns ON. But, if the pipe temperature remains high, once the time specified by ‘Delay before stop GC, if max water T°’ has elapsed ground cooling turns OFF.

Note: this facility safeguards against unusual or abnormal conditions causing operation of ground cooling (e.g. pipe in direct sunlight).

- TYP HTG    : 	Use this key to program settings for individual heating loops.

No Mixing Valve Modulation

- 4. Specify a ‘Start temperature’ equal to the required pipe temperature above which ground cooling turns ON.

Note: the origin of the temperature measurement is selected in the configuration menu for the heating loop, and is either the ground or ambient temperature sensor.

The ‘Stop temperature difference’ setting defines an offset below the start temperature to turn OFF ground cooling.

Note: the offset applies in this mode only.

Mixing Valve Modulation

- 5. The ‘3WV control time per °C’ settings specifies the amount of control per degree C of difference between the pipe and start (reference) temperatures.

Specify the maximum permitted change in the position of the valve over one control cycle.

## Configuration

COMPART    OTHER    OTHER    OTHER    COOLING   CONFIG

| This menu covers all compartments. Configuration heating comp 1 |  |  |  |  |  |  |  |  |  | 10 : 12 : 15 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Ground heating (3) |  |  |  |  |  |  |  |  |  |  |  |  |
| 3WV position start ground cooling [ 1 – 100% ] Minimum ON time [ 0 – 1439 min ] Modulate heating 3WV [ Yes / No ] |  |  |  |  |  |  | : : : | 10 2 YES |  |  |  | % min |
|  |  |  |  |  |  | MODIFY |  |  |  |  | QUIT |  |

Compressor start / stop

- The ‘3WV position start ground cooling’ setting specifies the mixing valve set-point that triggers the compressor to turn ON.

The compressor starts when at least one loop mixing valve set-point is above this threshold.

The compressor stops only when ALL mixing valve set-points are below the threshold.

- Specify a minimum ON time for the compressor.

Choose operating mode

- If ‘Modulate heating 3WV’ = Yes, control of the heating loop mixing valve is modulated. Otherwise, the mixing valve is not modulated and the pump is OFF.

### Reference temperatures if ground cooling enabled

IMPORTANT

When ground cooling is enabled the main temperature references for control of the heating loop are those programmed for ground cooling, that is:

Ground /Ambient T° set-point 	= ground cooling start T°

Max and min. water T°		= ground cooling max and min. water T°.

# AUXILIARY PERIOD

- Period of special working.

- Influences on ventilation and heating set-points.

- Start – end transition times.

## Setting up control

COMPART   OTHER    OTHER    OTHER    AUX PER

| 1. Enable the function and specify a period (start – end) of activation. Aux period settings compartment 1 |  |  |  |  |  |  |  |  |  | 10 : 12 : 15 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Ground heating (3) |  |  |  |  |  |  |  |  |  |  |  |  |
| Enable auxiliary period [ Yes / No ] Start time [ 00:00 / 23:59 ] End time [ 00:00 / 23:59 ] Transition time at start [ 0 – 120 min ] Transition time at end [ 0 – 120 min ] Influence on leeward ventilation T° [ -50/+50 °C] Influence on leeward vent min pos [ -100/+100 % ] Influence on windward ventil. T° [ -50/+50 °C] Influence on windward vent min pos [ -100 /+100 % ] Influence on T°, heating 1 [ -50/+50 °C ] Influence on min wtr T°, heating 1 [ -100/+100 °C ] Influence on T°, heating 2 [ -50/+50 °C ] Influence on min wtr T°, heating 2 [ -50/+50 °C ] |  |  |  |  |  |  | : : : | YES 10:00 17:30 10 10 0 0 0 0 0 0 0 0 |  |  |  | H/L/C H/L/C min min °C % °C % °C °C °C °C |
| N AUX |  |  |  |  |  | MODIFY |  |  |  |  | QUIT |  |

1

2

3

4

- 2. Program transition times to smooth the control changes at the start and end of the period.

- 3. Specify the amount of influence (increase or decrease) on the ventilation temperature set-point and minimum vent position applying to the leeward and windward vents during the auxiliary period.

- 4. Specify the amount of influence (increase or decrease) on the ambient temperature set-point and minimum water temperature applying to the high temperature and grow heating loops during the auxiliary period.

# AIR INFLATED WALLS

- ON/OFF control.

- Wind speed influence.

## Setting up control

COMPART   OTHER    KEY  1

| 1. Enable the function and specify a period (start – end) of activation. Air inflation settings compartment 1 |  |  |  |  |  |  |  |  |  | 10 : 12 : 15 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Activate air inflation [ Yes / No ] Start time [ 00:00 / 23:59 ] End time [ 00:00 / 23:59 ] ON time [ 0 – 1440 sec ] OFF (pause) time [ 0 – 500 min ] Wind speed for min influence [ 0 – 100 km/h ] Wind speed for max influence [ 0 – 100 km/h ] Maximum influence ON time [ 0 – 100 sec ] Maximum influence OFF time [ 0 – 100 min ] |  |  |  |  |  |  | : : : : : : : : : | NO 60 3 30 60 0 0 |  |  |  | T/R/S T/R/S sec min km/h km/h sec min |
|  |  |  |  |  |  | MODIFY |  |  |  |  | QUIT |  |

1

2

Specify the required blower ON and OFF times.

Wind influence

- 2. Specify the wind speed thresholds for minimum and maximum influence. The influence is proportional across the range.

Enter the maximum permitted change to the blower ON and OFF times..

# TEMPERATURE INTEGRATION

- Maintains a pre-set average compartment temperature over a specific period of time.

- Uses influences on the ambient and ventilation temperature set-points.

- Smooth start – end transitions.

## Setting up control

COMPART   OTHER    Key   2

| 1. Enable the function and specify a period (start – end) of activation. Temperature integration |  |  |  |  |  |  |  |  |  | 10 : 12 : 15 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Enable temperature integration [ Yes / No ] Start time [ 00:00 / 23:59 ] End time [ 00:00 / 23:59 ] Average temp. (integration steps) [ -50/+50 °C ] Inf. per degree difference [ -50/+50 °C ] Max inf. on ventilation temperature [ -50/+50 °C ] Max inf. on ambient temperature [ -50/+50 °C ] Transition (slope) time at start [ 0 / 1440 min ] Transition (slope) time at end [ 0 / 1440 min ] Number of integration steps [ 1 / 72 ] |  |  |  |  |  |  | : : : : : : : : : : | NO 18.0 1.0 3.0 1.5 15 15 24 |  |  |  | T/R/S T/R/S °C °C °C °C min min hrs |
|  |  |  |  |  |  | MODIFY |  |  |  |  | QUIT |  |

1

2

3

4

Specify the target average temperature.

- 2. Specify the amount of influence per degree difference between the measured average and target temperatures.

Specify the maximum permitted amount of influence (+ve or –ve) on the ventilation and ambient temperature set-points.

- 3. Program transition times to smooth the control changes at the start and end of the activation period.

- 4. Specify the ‘sliding’ time window in hours (steps) for the calculation of average temperature.

.

# MISCELLANEOUS FUNCTIONS

- Copy entries between identical menus (e.g. periods, heating, vents, compartments, boilers)

- Print out values of settings and averages (one-off or daily).

## How to Copy the Contents of Menus

In the source menu

- Press  MODIFY    then  to copy and quit the menu. The message 'COPY' below the time field indicates copy mode.

In the destination menu

- Press MODIFY  then to paste the new values. The 'COPY' message disappears.

## Printouts

SYSTEM    PRINT

| Select a particular compartment or all compartments. Settings printout menu |  |  |  |  |  |  |  |  |  | 10 : 12 : 15 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Printout compartment [ 1 – n° compart ] Printout all compartments [ Yes / No ] Heating [ Yes / No ] Vents [ Yes / No ] Humidity [ Yes / No ] Screens [ Yes / No ] Periods [ Yes / No ] Fog system [ Yes / No ] Circulation fan [ Yes / No ] Lighting [ Yes / No ] CO2 [ Yes / No ] Alarms [ Yes / No ] Boiler [ Yes / No ] Weather Station [ Yes / No ] |  |  |  |  |  |  | : : : : : : : : : : : : : : | 1 YES YES YES YES NO YES NO NO NO NO YES NO YES |  |  |  |  |
| START |  |  |  | OTHER |  | MODIFY |  |  |  |  | QUIT |  |

Enter ‘Yes’ against a category to include the settings in the printout.

- Press the START key to request an immediate printout.

### Averages

SYSTEM    PRINT  OTHER

| Select a particular compartment or all compartments. Settings printout menu |  |  |  |  |  |  |  |  |  | 10 : 12 : 15 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Printout compartment [ 1 – n° compart ] Printout all compartments [ Yes / no ] Printout the averages [ Yes / no ] Printout averages daily [ Yes / no ] |  |  |  |  |  |  | : : : : | 1 NO NO YES |  |  |  |  |
| START |  |  |  |  |  | MODIFY |  |  |  |  | QUIT |  |

‘Printout averages daily‘ = Yes results in a  daily printout of averages at the start of period 1.

- Press the START key to request an immediate printout.

See ‘Aux’ in the Windows boiler settings

2 see ‘Cascade’ in the Windows boiler settings